## TITLE
COLLEGE OF TECHNOLOGY AT FARMINGDALE
SCHOOL OF APPLIED SOCIAL SCIENCES
NET ZERO CARBON STUDY
Farmingdale, New York
SUCF Project #26325
Concept Estimate
2021-03-08

## BOE
| COLLEGE OF TECHNOLOGY AT FARMINGDALE |  | 2021-03-08
NET ZERO CARBON STUDY
BASIS OF ESTIMATE (B.O.E.)
1 | SCC Concept Estimate is based on the following documents prepared by Urbahn Architects
Net Zero Carbon Study- Draft Report dated 12/23/2020
2 | Project Areas & Scope
a. | Option-1: Centralized Ground Source HVAC
b. | Option-2: Centralized Air Source HVAC
c. | Option-3: Distributed Heat Pump System
3 | Estimate does excludes the following
a. | Design fee
b. | Overtime cost
c. | Environmental Abatements
d. | Artwork, Graphics, Banners and Flags
e. | Rock Excavation
f. | Dewatering
g. | Signage & Painting
h. | Construction contingency
4 | Construction Schedule
| Construction State Date | 2021-12-01
| Construction Mid Point Date | 2023-03-01
| Construction End Date | 2024-06-01
5 | Markups
The following Markups are included
| General Conditions | 10%
| General Contractor's Overhead & Profit | 8%
| Design Contingency | 10%
| Bid Contingency | 5%
| Escalation to the Midpoint | 8.438%
Escalation Rate 3.75% per year

## SUM
| COLLEGE OF TECHNOLOGY AT FARMINGDALE |  |  |  |  | 2021-03-08
NET ZERO CARBON STUDY
Concept Estimate
SUMMARY OF TRADES
| Description |  | Option-1 | Option-2 | Option-3 | Base Option
1 | 01-00-00 General Requirements |  | 2599528.9048 | 2395183.5546 | 2291411.5709 | 2573215.5769 |  |  |  | 26313.3279 | -178032.0223 | -281804.0059
2 | 02-00-00 Existing Conditions |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
3 | 03-00-00 Concrete |  | 2463438.74 | 2394333.1374 | 2394333.1374 | 2463244.8261 |  |  |  | 193.9139 | -68911.6887 | -68911.6887
4 | 04-00-00 Masonry |  | 826463.26 | 805240.86 | 805240.86 | 826644.9396 |  |  |  | -181.6796 | -21404.0796 | -21404.0796
5 | 05-00-00 Metals |  | 4147196 | 3988939.96 | 3957546.52 | 4122195.5848 |  |  |  | 25000.4152 | -133255.6248 | -164649.0648
6 | 06-00-00 Wood, Plastics, & Composites |  | 386314.25 | 376394.25 | 376394.25 | 386209.574 |  |  |  | 104.676 | -9815.324 | -9815.324
7 | 07-00-00 Thermal and Moisture Protection |  | 2013988 | 2007895.2 | 2007895.2 | 2013988.0394 |  |  |  | -0.03945 | -6092.8394 | -6092.8394
8 | 08-00-00 Openings |  | 1787408 | 1783506.825 | 1759961.745 | 1787407.8331 |  |  |  | 0.16692 | -3901.0081 | -27446.0881
9 | 09-00-00 Finishes |  | 2798966 | 2733592.7775 | 2733592.7775 | 2792966.2724 |  |  |  | 5999.7276 | -59373.4949 | -59373.4949
10 | 10-00-00 Specialties |  | 159011.93 | 154928.73 | 154928.73 | 158947.35 |  |  |  | 64.58 | -4018.62 | -4018.62
11 | 11-00-00 Equipments |  | 129602.2 | 126274.2 | 126274.2 | 129537.5 |  |  |  | 64.7 | -3263.3 | -3263.3
12 | 12-00-00 Furnishings |  | 176956.85 | 172412.85 | 172412.85 | 176970.8 |  |  |  | -13.95 | -4557.95 | -4557.95
13 | 13-00-00 Special Construction |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
14 | 14-00-00 Elevators |  | 607136.46 | 591546.06 | 591546.06 | 607375 |  |  |  | -238.54 | -15828.94 | -15828.94
15 | 21-00-00 Fire Suppression |  | 509436.34 | 496354.74 | 496354.74 | 509383.6438 |  |  |  | 52.6962 | -13028.9037 | -13028.9037
16 | 22-00-00 Plumbing |  | 854469.38 | 833298.18 | 833298.18 | 824473.5849 |  |  |  | 29995.7951 | 8824.5951 | 8824.5951
17 | 23-00-00 Heating, Ventilation, & Air Conditioning (HVAC) |  | 4796399.79 | 4812099.79 | 3858768.04 | 5775993.2332 |  |  |  | -979593.4432 | -963893.4432 | -1917225.1932
18 | 26-00-00 Electrical |  | 2539348.4015 | 2476522.4953 | 2447072.9288 | 2554638.4607 |  |  |  | -15290.0591 | -78115.9654 | -107565.5319
19 | 27-00-00 Communications |  | 168981.33 | 164642.13 | 164642.13 | 168903.8409 |  |  |  | 77.4891 | -4261.7109 | -4261.7109
20 | 28-00-00 Electronic Safety & Security |  | 433170.43 | 422047.23 | 422047.23 | 433275.2858 |  |  |  | -104.8558 | -11228.0558 | -11228.0558
21 | 31-00-00 Earthwork |  | 0 | -49395.5556 | -49395.5556 |  |  |  |  | 0 | -49395.5556 | -49395.5556
22 | 32-00-00 Exterior Improvements |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0
23 | 33-00-00 Utilities |  | 1197001.6862 | -338798.3138 | -338798.3138 |  |  |  |  | 1197001.6862 | -338798.3138 | -338798.3138
24 |  |  | - | - | - | -
25 | Subtotal 1 |  | 28594817.9525 | 26347019.1004 | 25205527.2803 | 28305371.3455 |  | 22914115.7093 |  | 289446.607 | -1958352.245 | -3099844.0652
26 | General Contractor's Office Overhead & Profit | 8% | 2287585.4362 | 2107761.528 | 2016442.1824 | 2264429.7076
27 |  |  | - | - | - | -
28 | Subtotal 2 |  | 30882403.3887 | 28454780.6285 | 27221969.4627 | 30569801.0531
29 | Design Contingency | 10% | 3088240.3389 | 2845478.0628 | 2722196.9463 | 0
30 |  |  | - | - | - | -
31 | Subtotal 3 |  | 33970643.7275 | 31300258.6913 | 29944166.409 | 30569801.0531
32 | Escalation to (Midpoint of Construction) | 8.438% | 2866273.0645 | 2640959.3271 | 2526539.0408 | 2579326.9639
33 |  |  | - | - | - | -
34 | Total CONSTRUCTION Cost |  | 36836916.7921 | 33941218.0184 | 32470705.4497 | 33149128.017
35 | Bid Contingency | 5% | 1841845.8396 | 1697060.9009 | 1623535.2725 | 1657456.4008 |  |  | 1.4874
36 |  |  | - | - | - | -
37 | Total CONSTRUCTION Cost w/Bid Contingency |  | 38678762.6317 | 35638278.9193 | 34094240.7222 | 34806584.4178 | 1.3526 | 0.14879
| Site Work |  | 9580614.4967 | 9580614.4967 | 9580614.4967 | 9580614.4967 |  |  |  |  | 38665386.6907
| TOTAL Construction cost w/Bid Contingency (& Site Work) |  | 48259377.1283 | 45218893.416 | 43674855.2189 | 44387198.9145
| Total Gross Area in SF |  | 49847 | 48567 | 48567 | 49847
| Construction Cost per GSF |  | 738.9997 | 698.8535 | 668.5755 | 665.0175
| Cost per GSF w/Bid Contingency |  | 775.9497 | 733.7962 | 702.0043 | 698.2684

## EST
COLLEGE OF TECHNOLOGY AT FARMINGDALE
Farmingdale, New York
| Concept Estimate | [7 empty] | 2021-03-08
| NET ZERO CARBON STUDY |  |  | 49847 | SF | 48567 | SF | 48567 | SF
| Description | Unit Price | Unit | Option-1 |  | Option-2 |  | Option-3 | Amount
|  |  |  | Quantity | Amount | Quantity | Amount | Quantity | Amount
1
2 | 01-00-00 General Requirements
3
4 | Site General Conditions - 10% | 1 | LS | 2599528.9048 | 2599528.9048 | 2395183.5546 | 2395183.5546 | 2291411.5709 | 2291411.5709
5 |  |  |  |  | - |  | - |  | -
6 | Subtotal 01-00-00 General Requirements |  |  |  | 2599528.9048 |  | 2395183.5546 |  | 2291411.5709
7
8 | 02-00-00 Existing Conditions
9
10 |  |  |  |  | 0 |  | 0 |  | 0
11 |  |  |  |  | - |  | - |  | -
12 | Subtotal 02-00-00 Existing Conditions |  |  |  | 0 |  | 0 |  | 0
13
14 | 03-00-00 Concrete
15 | Concrete revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
16
17 | DEDUCT
18 | Concrete slab on grade at basement - 1,400 SF + 460 SF - Options 2 & 3 | 12.5775 | SF | 0 | 0 | -1860 | -23394.15 | -1860 | -23394.15 | GM
19
20 | Concrete fill on deck at first floor - 820 SF (exclude areaway) + 460 SF - Options 2 & 3 | 10.062 | SF | 0 | 0 | -1280 | -12879.36 | -1280 | -12879.36 | GM
21
22 | Concrete foundation walls / areaway walls at basement - Options 2 & 3 | 1259.9 | CY | 0 | 0 | -36.7407 | -46289.6593 | -36.7407 | -46289.6593 | GM
23 | Deduct - 236 LF x 16' high x 1' th / Add 174 LF x 16' high x 1' th
24
25 | Concrete encasement of steel columns at basement reduced building perimeter walls - Options 2 & 3 | 1386.75 | CY | 0 | 0 | -3 | -4160.25 | -3 | -4160.25 | GM
26 | Deduct - 1' x 1' x 15' high x 5 each
27
28 | Concrete perimeter wall footings at building and areaway walls at basement - Options 2 & 3 | 1006.2 | CY | 0 | 0 | -5.7407 | -5776.3333 | -5.7407 | -5776.3333 | GM
29 | Deduct - 236 LF x 2.5' x 1' / Add 174 LF x 2.5' x 1'
30
31 | ADD
32
33 | Add back concrete slab on grade at first floor- 1,400 SF + 460 SF (Note : 820 SF of this will be in site at deleted areaway) - Options 2 & 3 | 12.5775 | SF | 0 | 0 | 1860 | 23394.15 | 1860 | 23394.15 | GM
34
35 | Concrete Construction | 2463438.74 | LS | 1 | 2463438.74 | 1 | 2463438.74 | 1 | 2463438.74
36 |  |  |  |  | - |  | - |  | -
37 | Subtotal 03-00-00 Concrete |  |  |  | 2463438.74 |  | 2394333.1374 |  | 2394333.1374
38
39 | 04-00-00 Masonry
40
41 | Masonry Construction | 16.58 | SF | 49847 | 826463.26 | 48567 | 805240.86 | 48567 | 805240.86
42 |  |  |  |  | - |  | - |  | -
43 | Subtotal 04-00-00 Masonry |  |  |  | 826463.26 |  | 805240.86 |  | 805240.86
44
45 | 05-00-00 Metals
46
47
48 | Structural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
49
50 | DEDUCT
51 | Structural steel beam and column framing at first floor- (1,400 SF + 460 SF) x 17 LB / SF - Options 2 & 3 | 6450 | TON | 0 | 0 | -16 | -103200 | -16 | -103200 | GM
53 | Crane to lift structural steel - (1,400 SF + 460 SF) x 17 LB / SF - Options 2 & 3 | 447.2 | TON | 0 | 0 | -16 | -7155.2 | -16 | -7155.2 | GM
55 | 3" Galvanized metal deck at first floor - 820 SF (exclude areaway) + 460 SF - Options 2 & 3 | 6.708 | SF | 0 | 0 | -1280 | -8586.24 | -1280 | -8586.24 | GM
56
57 | 1 1/2" Steel grating at deleted south areaway - Options 2 & 3 | 72.67 | SF | 0 | 0 | -440 | -31974.8 | -440 | -31974.8 | GM
58
59 | Galvanized steel framing at above areaway grating - allow 5 LBS / SF - Options 2 & 3 | 3.354 | LB | 0 | 0 | -2200 | -7378.8 | -2200 | -7378.8 | GM
60
61 | Steel ladder and hatch at deleted south areaway - Options 2 & 3 | 2236 | EA | 0 | 0 | -1 | -2236 | -1 | -2236 | GM
62
63 | Galvanized steel framing at added rooftop screen wall - allow 20 LBS / SF - Options 2 & 3 | 3.354 | LB | 0 | 0 | 0 | 0 | -5460 | -18312.84 | GM
64 | Option 3 - 21LF x 13' high x 20 LB / SF
65
66 | ADD
67 | Allowance of two tons of structural steel at roof for new dunnage and huskier roof beams under dunnage - As per Architect - Options 2 & 3 | 6450 | TON | 0 | 0 | 2 | 12900 | 2 | 12900 | GM
69 | Crane to lift structural steel - two tons - Options 2 & 3 | 447.2 | TON | 0 | 0 | 2 | 894.4 | 2 | 894.4 | GM
71 | Exterior paint for structural steel - two tons - Options 2 & 3 | 200 | TON | 0 | 0 | 2 | 400 | 2 | 400 | GM
72
73 | Galvanized steel framing at added rooftop screen wall - allow 20 LBS / SF - Option 2 | 3.354 | LB | 0 | 0 | 3900 | 13080.6 | 0 | 0 | GM
74 | Option 2 - 15 LF x 13' high x 20 LB / SF
76 | Reorganize and redesign roof structural framing at three rooftop AHU units as per note by LERA on Option No. 1 drawing A-104 Cannot quantify this item | 25000 | LS | 1 | 25000 |  | 0 |  | 0 | GM
77
78 | Steel Construction | 4122196 | LS | 1 | 4122196 | 1 | 4122196 | 1 | 4122196
79 |  |  |  |  | - |  | - |  | -
80 | Subtotal 05-00-00 Metals |  |  |  | 4147196 |  | 3988939.96 |  | 3957546.52
81
82 | 06-00-00 Wood, Plastics, & Composites
83
84 | Architectural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
85
86 | DEDUCT
87 | Rough carpentry | 7.75 | SF | 49847 | 386314.25 | 48567 | 376394.25 | 48567 | 376394.25
88 |  |  |  |  | - |  | - |  | -
89 | Subtotal 06-00-00 Wood, Plastics, & Composites |  |  |  | 386314.25 |  | 376394.25 |  | 376394.25
90
91 | 07-00-00 Thermal and Moisture Protection
92
93 | Architectural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north
94
95 | DEDUCT
96 | Deduct fireproofing and fire stopping based on reduced gross enclosed area at basement - Options 2 & 3 | 1.55 | SF |  | 0 | -1280 | -1984 | -1280 | -1984 | GM
97
98 | Deduct waterproofing based on reduced gross enclosed area at basement - Options 2 & 3 | 1.4 | SF |  | 0 | -1280 | -1792 | -1280 | -1792 | GM
99
100 | Deduct insulation, caulking and sealants based on reduced gross enclosed area at basement - Options 2 & 3 | 1.81 | SF |  | 0 | -1280 | -2316.8 | -1280 | -2316.8 | GM
101
102 | Assume no exterior wall revisions at first floor - Options 1, 2 & 3 | [5 empty] | No work |  | No work | GM
103
104 | Thermal & Moisture protection | 2013988 | SF | 1 | 2013988 | 1 | 2013988 | 1 | 2013988
105 |  |  |  |  | - |  | - |  | -
106 | Subtotal 07-00-00 Thermal and Moisture Protection |  |  |  | 2013988 |  | 2007895.2 |  | 2007895.2
107
108 | 08-00-00 Openings
109
110 | Architectural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
111
112 | DEDUCT
113 | Furnish and install single flush insulated hollow metal core doors and frames including all finish hardware at basement areaways - Options 2 & 3 | 2746.625 | EA |  | 0 | -1 | -2746.625 | -1 | -2746.625 | GM
114
115 | Furnish and install double flush insulated hollow metal core doors and frames including all finish hardware at basement areaways - Options 2 & 3 | 5482.5 | PR |  | 0 | -2 | -10965 | -2 | -10965 | GM
116
117 | EXTERIOR SCREEN WALL AT ROOF
118 | Exterior roof wall screen assembly with UHPC ultra high performance panels at new cooling tower at roof - Structural framing separate - Option 3 | 50.31 | EA |  | 0 | 0 | 0 | -273 | -13734.63 | GM
119 | Option 3 - 21 LF x 13' high - credit
120
121 | ADD
122 | EXTERIOR SCREEN WALL AT ROOF
123 | Exterior roof wall screen assembly with UHPC ultra high performance panels at new cooling tower at roof - Structural framing separate - Option 2 | 50.31 | EA |  | 0 | 195 | 9810.45 | 0 | 0 | GM
124 | Option 2 - 15 LF x 13' high
125
126 | Interior & Exterior doors,windows & Curtain wall | 1787408 | LS | 1 | 1787408 | 1 | 1787408 | 1 | 1787408
127 |  |  |  |  | - |  | - |  | -
128 | Subtotal 08-00-00 Openings |  |  |  | 1787408 |  | 1783506.825 |  | 1759961.745
129
130 | 09-00-00 Finishes
131
132 | Architectural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
133
134 | DEDUCT
135 | WALLS
136 | Type 2A,2B: Corridor partition - 2 layers 5/8" GWB / 3 5/8" metal studs / batt insulation / 2 layers 5/8" GWB - impact & mold resistant - Note: These walls are deducted because foundation walls at basement at pushed back because of reduced enclosed area - 150 LF x 15' ht - Options 2 & 3 | 21.1453 | SF | 0 | 0 | -2250 | -47576.8125 | -2250 | -47576.8125 | GM
137
138 | FLOOR FINISHES
139 | Paint concrete at exposed concrete floors at basement (exclude areaway) - Options 2 & 3 | 5.375 | SF |  | 0 | -1280 | -6880 | -1280 | -6880 | GM
140
141 | WALL FINISHES
142 | Prime and paint interior gypsum board walls - Options 2 & 3 | 1.6125 | SF |  | 0 | -4500 | -7256.25 | -4500 | -7256.25 | GM
143
144 | CEILINGS
145 | Paint exposed ceilings at basement - Options 2 & 3 | 2.8595 | SF |  | 0 | -1280 | -3660.16 | -1280 | -3660.16 | GM
146
147 | ADD
148
149 | WALLS
150 | Vertical shaftwall enlargement at second and third floors - 3 locations - Options 1, 2 & 3 | 2000 | LOC | 3 | 6000 | 3 | 6000 | 3 | 6000 | GM
151
152 | Wall, Floor & Ceiling finishes | 2792966 | SF | 1 | 2792966 | 1 | 2792966 | 1 | 2792966
153 |  |  |  |  | - |  | - |  | -
154 | Subtotal 09-00-00 Finishes |  |  |  | 2798966 |  | 2733592.7775 |  | 2733592.7775
155
156 | 10-00-00 Specialties
157
158 | Architectural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
159
160 | Toilet partitions, Accessories & Signage | 3.19 | SF | 49847 | 159011.93 | 48567 | 154928.73 | 48567 | 154928.73
161 |  |  |  |  | - |  | - |  | -
162 | Subtotal 10-00-00 Specialties |  |  |  | 159011.93 |  | 154928.73 |  | 154928.73
163
164 | 11-00-00 Equipments
165
166 | Equipment | 2.6 | SF | 49847 | 129602.2 | 48567 | 126274.2 | 48567 | 126274.2
167 |  |  |  |  | - |  | - |  | -
168 | Subtotal 11-00-00 Equipments |  |  |  | 129602.2 |  | 126274.2 |  | 126274.2
169
170 | 12-00-00 Furnishings
171
172 | Furnishings | 3.55 | SF | 49847 | 176956.85 | 48567 | 172412.85 | 48567 | 172412.85
173 |  |  |  |  | - |  | - |  | -
174 | Subtotal 12-00-00 Furnishings |  |  |  | 176956.85 |  | 172412.85 |  | 172412.85
175
176 | 13-00-00 Special Construction
177
178 |  |  |  |  | - |  | - |  | -
179 | Subtotal 13-00-00 Special Construction |  |  |  | 0 |  | 0 |  | 0
180
181 | 14-00-00 Elevators
182
183 | Conveying System | 12.18 | SF | 49847 | 607136.46 | 48567 | 591546.06 | 48567 | 591546.06
184 |  |  |  |  | - |  | - |  | -
185 | Subtotal 14-00-00 Elevators |  |  |  | 607136.46 |  | 591546.06 |  | 591546.06
186
187 | 21-00-00 Fire Suppression
188
189 | Fire supression revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north
190
191 | Fire Protection | 10.22 | SF | 49847 | 509436.34 | 48567 | 496354.74 | 48567 | 496354.74
192 |  |  |  |  | - |  | - |  | -
193 | Subtotal 21-00-00 Fire Suppression |  |  |  | 509436.34 |  | 496354.74 |  | 496354.74
194
195 | 22-00-00 Plumbing
196
197 | Plumbing | 16.54 | SF | 49847 | 824469.38 | 48567 | 803298.18 | 48567 | 803298.18
198 | ADD
199 | Electric Domestic water heater, associated piping. (Add to the base to replace the heat exchanger) | 30000 | Allow | 1 | 30000 | 1 | 30000 | 1 | 30000
200 |  |  |  |  | - |  | - |  | -
201 | Subtotal 22-00-00 Plumbing |  |  |  | 854469.38 |  | 833298.18 |  | 833298.18
202
203 | 23-00-00 Heating, Ventilation, & Air Conditioning (HVAC)
204
205 | ADD
206 | Geothermal pump and controls | 50000 | LS | 1 | 50000 |  | 0 | 0 | 0
207 | Heat recovery Chiller - 120 Ton, Model#TPWCCMV0600T-MM-HR-3HX (Option-1) | 263500 | EA | 1 | 263500 |  | 0 | 0 | 0
208 | Air Cooled Heat recovery Chiller - 120 Ton, Model#TPACVMV0300T3-MM-HR-VS (Option-2) | 410000 | EA |  | 0 | 1 | 410000 | 0 | 0
209 | RTAH-1,2,3 Roof Top Air Handling Unit - 11,000 CFM, 40 Ton (Option-1 &2) | 159500 | EA | 3 | 478500 | 3 | 478500 | 0 | 0 |  | 13.1818
210 | Pre-treatment loops | 66000 | LS | 1 | 66000 |  | 0 | 0 | 0
211 | Air Source Heat Pump Chiller,120 ton | 260000 | EA |  | 0 |  | 0 | 1 | 260000
212 | Horizon-Air Source Heat Pump, DOAS, 8250 cfm. Model#OANE648A3-C1C400JR-00000AC7JR2G50BOB5CO | 174000 | EA |  | 0 |  | 0 | 1 | 174000
213 | WSHP, Water souce heat pump, 1-10 mbh | 3500 | EA |  | 0 |  | 0 | 33 | 115500
214 | WSHP, Water souce heat pump, 11-20 mbh | 4500 | EA |  | 0 |  | 0 | 6 | 27000
215 | WSHP, Water souce heat pump, 21-30 mbh | 5500 | EA |  | 0 |  | 0 | 12 | 66000
216 | Condenser water loop S/R piping and insulation, Main | 180 | LF | 0 | 0 |  | 0 | 2500 | 450000
217 | Condenser water loop S/R piping and insulation, Branch | 105 | LF | 0 | 0 |  | 0 | 2000 | 210000
218 | Cond. Drain piping, pump, valves, Pan, supports | 3150 | EA | 0 | 0 |  | 0 | 51 | 160650
219 | Refrigerant piping | 89250 | LS | 0 | 0 |  | 0 | 1 | 89250
220 | Rigging | 30000 | EA | 0 | 0 | 1 | 30000 | 1 | 30000
221
222 | DEDUCT |  |  |  | 0 |  | 0 |  | 0
223 | CT-1,2 Cooling Towers and SSF-1 Side-Stream Filter | -215198 | LS | 1 | -215198 | 1 | -215198 | 1 | -215198
224 | CH-1,2 Water Cooled Liquid Chiller - 100 Ton, 240/300 GPM | -151680.25 | EA | 2 | -303360.5 | 2 | -303360.5 | 2 | -303360.5
225 | AHU-1,2,3 Air Handling Unit - 15,900 CFM, 55 Ton incl. Sound Attenuators | -283927.57 | EA | 3 | -851782.71 | 3 | -851782.71 | 3 | -851782.71 |  | -17.8571
226 | HX-1,2 Heat Exchanger, Shell and Tube - 575 MBH | -15770.25 | EA | 2 | -31540.5 | 2 | -31540.5 | 2 | -31540.5
227 | HX-3,4 Heat Exchanger, Shell and Tube - 1,764 MBH | -26445 | EA | 2 | -52890 | 2 | -52890 | 2 | -52890
228 | PRVS-1 and valves | -90000 | LS | 1 | -90000 | 1 | -90000 | 1 | -90000
229 | CWS/R Piping | -85734 | LS | 1 | -85734 | 1 | -85734 | 1 | -85734
230 | Duct and insulation reduction due to reduced CFM, option-1&-2 | -82123.5 | LS | 1 | -82123.5 | 1 | -82123.5 |  | 0
231 | Duct and insulation reduction, option-3 | -656988 | LS |  | 0 |  | 0 | 1 | -656988
232 | Duct accessories, Supply Diffuser/Return Register, Dampers, option-3 | -37492.25 | LS |  | 0 |  | 0 | 1 | -37492.25
233 | VAV Boxes w/reheat coil, option-3 | -137498 | LS |  | 0 |  | 0 | 1 | -137498
234 | MPS/LPS/LPC and vent Piping | -61646 | LS | 1 | -61646 | 1 | -61646 | 1 | -61646
235 | Equipment connections, Cooling towers, Heat Exchangers | -63318 | LS | 1 | -63318 | 1 | -63318 | 1 | -63318
236 | HWS/R Piping, option-3 | -521288 | LS |  | 0 |  | 0 | 1 | -521288
237 | CHWS/R Piping, option-3 | -228069 | LS |  | 0 |  | 0 | 1 | -228069
238 | Chilled water pump, Heating hot water pump, Pre-heat water pump, option-3 | -28020 | LS |  | 0 |  | 0 | 1 | -28020
239 | BMS system. DDC Controls w/ Programming, Tie-In, Headend Equipment, etc., option-3 | -90000 | LS |  | 0 |  | 0 | 1 | -90000
240
241 | HVAC revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north
242 | DEDUCT
243
244 | Venting and heating based on reduced gross enclosed area at basement at Option 2 and Option 3 (Exclude areaway ) - use 1,280 SF | 35 | SF |  | 0 | -1280 | -44800 | -1280 | -44800 | GM
245
246 | HVAC | 5775993 | SF | 1 | 5775993 | 1 | 5775993 | 1 | 5775993
247 |  |  |  |  | - |  | - |  | -
248 | Subtotal 23-00-00 Heating, Ventilation, & Air Conditioning (HVAC) |  |  |  | 4796399.79 |  | 4812099.79 |  | 3858768.04
249
250 | 26-00-00 Electrical
251
252 | ADD ( Option 1 Criteria ) |  |  |  | 0 |  | 0 |  | 0
253 | Chiller ( In Basement ) |  |  |  | 0 |  | 0 |  | 0
254 | Disconnect Switch - 250A | 2500 | EA | 1 | 2500 |  | 0 |  | 0
255 | MDB to Chiller -2-1/2"EMT - 3#350MCM, #3 |  |  |  | 0 |  | 0 |  | 0
256 | 2-1/2"EMT | 27.93 | LF | 150 | 4189.5 |  | 0 |  | 0
257 | #350MCM | 15.5 | LF | 450 | 6975 |  | 0 |  | 0
258 | #3 | 3.95 | LF | 150 | 592.5 |  | 0 |  | 0
259 | CHWP 1,2 ( Allow 2 Pumps ) |  |  |  | 0 |  | 0 |  | 0
260 | 10HP - VFD Install Only | 1191.96 | EA | 2 | 2383.92 |  | 0 |  | 0
261 | 3/4"EMT - 4#12 - CHWP 1,2 to PPHB |  |  |  | 0 |  | 0 |  | 0
262 | 3/4"EMT | 11.3784 | LF | 55 | 625.8145 |  | 0 |  | 0
263 | #12 | 1.1849 | LF | 220 | 260.6703 |  | 0 |  | 0
264 | AHU 1,2,3 |  |  |  | 0 |  | 0 |  | 0
265 | PPAH-1,2,,3 ( Panels for AHU ) - 75A - Allow | 3000 | EA | 3 | 9000 |  | 0 |  | 0
266 | PPH3 to PP-AH1,2,3 - 3#4, #8 - 1"EMT |  |  |  | 0 |  | 0 |  | 0
267 | 1"EMT | 13.3563 | LF | 350 | 4674.7181 |  | 0 |  | 0
268 | #4 | 3.5374 | LF | 1050 | 3714.3224 |  | 0 |  | 0
269 | #8 | 2.1136 | LF | 350 | 739.7602 |  | 0 |  | 0
270 | 5HP VFD - Install Only | 1100 | EA | 6 | 6600 |  | 0 |  | 0
271 | AHU1,2,3 to 5HP VFD - 3/4"EMT - 4#12 |  |  |  | 0 |  | 0 |  | 0
272 | 3/4"EMT | 11.3784 | LF | 65 | 739.5989 |  | 0 |  | 0
273 | #12 | 1.1849 | LF | 260 | 308.0649 |  | 0 |  | 0
274 | 10HP VFD - Install Only | 1191.96 | EA | 6 | 7151.76 |  | 0 |  | 0
275 | AHU1,2,3 to 10HP VFD - 3/4"EMT - 4#10 |  |  |  | 0 |  | 0 |  | 0
276 | 3/4"EMT | 11.3784 | LF | 150 | 1706.7667 |  | 0 |  | 0
277 | #12 | 1.1849 | LF | 600 | 710.919 |  | 0 |  | 0
278 |  |  |  |  | 0 |  | 0 |  | 0
279 | Deduct ( Base Set ) |  |  |  | 0 |  | 0 |  | 0
280 | Chiller 1, 2 |  |  |  | 0 |  | 0 |  | 0
281 | Disconnect Switch - 250A | 1364.6742 | EA | -2 | -2729.3485 |  | 0 |  | 0
282 | MDB to Chiller - 2"EMT - 3#3/0, 1#4 |  |  |  | 0 |  | 0 |  | 0
283 | 2"EMT | 20.3622 | LF | -300 | -6108.6595 |  | 0 |  | 0
284 | #3/0 | 9.0912 | LF | -900 | -8182.1243 |  | 0 |  | 0
285 | #4 | 3.5374 | LF | -300 | -1061.235 |  | 0 |  | 0
286 | CHWP 1,2,3 |  |  |  | 0 |  | 0 |  | 0
287 | 10HP - VFD Install Only | 1191.96 | EA | -3 | -3575.88 |  | 0 |  | 0
288 | 3/4"EMT - 4#12 - CHWP 1,3 to PPHB |  |  |  | 0 |  | 0 |  | 0
289 | 3/4"EMT | 11.3784 | LF | -60 | -682.7067 |  | 0 |  | 0
290 | #12 | 1.1849 | LF | -240 | -284.3676 |  | 0 |  | 0
291 | 3/4"EMT - 4#10 - CHWP 2 to PPHB |  |  |  | 0 |  | 0 |  | 0
292 | 3/4"EMT | 11.3784 | LF | -30 | -341.3533 |  | 0 |  | 0
293 | #12 | 1.1849 | LF | -120 | -142.1838 |  | 0 |  | 0
294 | AHU 1,2,3 |  |  |  | 0 |  | 0 |  | 0
295 | PPAH-1,2,,3 ( Panels for AHU ) - 100A | 3984.925 | EA | -3 | -11954.775 |  | 0 |  | 0
296 | PPH3 to PP-AH1,2,3 - 3#2, #8 - 1-1/2"EMT |  |  |  | 0 |  | 0 |  | 0
297 | 1-1/2"EMT | 17.9065 | LF | -350 | -6267.2715 |  | 0 |  | 0
298 | #2 | 4.5399 | LF | -1050 | -4766.8492 |  | 0 |  | 0
299 | #8 | 2.1136 | LF | -350 | -739.7602 |  | 0 |  | 0
300 | 7.5HP VFD - Install Only | 1191.96 | EA | -6 | -7151.76 |  | 0 |  | 0
301 | AHU1,2,3 to 7.5HP VFD - 3/4"EMT - 4#12 |  |  |  | 0 |  | 0 |  | 0
302 | 3/4"EMT | 11.3784 | LF | -65 | -739.5989 |  | 0 |  | 0
303 | #12 | 1.1849 | LF | -260 | -308.0649 |  | 0 |  | 0
304 | 15HP VFD - Install Only | 1489.95 | EA | -6 | -8939.7 |  | 0 |  | 0
305 | AHU1,2,3 to 15HP VFD - 3/4"EMT - 4#10 |  |  |  | 0 |  | 0 |  | 0
306 | 3/4"EMT | 11.3784 | LF | -150 | -1706.7667 |  | 0 |  | 0
307 | #10 | 1.5861 | LF | -600 | -951.633 |  | 0 |  | 0
308 | Junction Box - Heat Exchanger | 65.0482 | EA | -4 | -260.193 |  | 0 |  | 0
309 | 3/4"EMT | 11.3784 | LF | -80 | -910.2756 |  | 0 |  | 0
310 | #12 | 1.1849 | LF | -320 | -379.1568 |  | 0 |  | 0
311 | [6 empty] | 0 |  | 0
312 | Add ( Option 2 Criteria ) | [5 empty] | 0 |  | 0
313 | Chiller ( In Roof ) | [5 empty] | 0 |  | 0
314 | Disconnect Switch - 250A | 2500 | EA |  |  | 1 | 2500 |  | 0
315 | MDB to Chiller -2-1/2"EMT - 3#350MCM, #3 | [5 empty] | 0 |  | 0
316 | 2-1/2"EMT | 27.93 | LF |  |  | 120 | 3351.6 |  | 0
317 | #350MCM | 15.5 | LF |  |  | 360 | 5580 |  | 0
318 | #3 | 3.95 | LF |  |  | 120 | 474 |  | 0
319 | CHWP 1,2 ( Allow 2 Pumps ) | [5 empty] | 0 |  | 0
320 | 10HP - VFD Install Only | 1191.96 | EA |  |  | 2 | 2383.92 |  | 0
321 | 3/4"EMT - 4#12 - CHWP 1,2 to PPHB | [5 empty] | 0 |  | 0
322 | 3/4"EMT | 11.3784 | LF |  |  | 373 | 4244.16 |  | 0
323 | #12 | 1.1849 | LF |  |  | 1492 | 1767.8186 |  | 0
324 | AHU 1,2,3 | [5 empty] | 0 |  | 0
325 | PPAH-1,2,,3 ( Panels for AHU ) - 75A - Allow | 3000 | EA |  |  | 3 | 9000 |  | 0
326 | PPH3 to PP-AH1,2,3 - 3#4, #8 - 1"EMT | [5 empty] | 0 |  | 0
327 | 1"EMT | 13.3563 | LF |  |  | 350 | 4674.7181 |  | 0
328 | #4 | 3.5374 | LF |  |  | 1050 | 3714.3224 |  | 0
329 | #8 | 2.1136 | LF |  |  | 350 | 739.7602 |  | 0
330 | 5HP VFD - Install Only | 1100 | EA |  |  | 6 | 6600 |  | 0
331 | AHU1,2,3 to 5HP VFD - 3/4"EMT - 4#12 | [5 empty] | 0 |  | 0
332 | 3/4"EMT | 11.3784 | LF |  |  | 65 | 739.5989 |  | 0
333 | #12 | 1.1849 | LF |  |  | 260 | 308.0649 |  | 0
334 | 10HP VFD - Install Only | 1191.96 | EA |  |  | 6 | 7151.76 |  | 0
335 | AHU1,2,3 to 10HP VFD - 3/4"EMT - 4#10 | [5 empty] | 0 |  | 0
336 | 3/4"EMT | 11.3784 | LF |  |  | 150 | 1706.7667 |  | 0
337 | #12 | 1.1849 | LF |  |  | 600 | 710.919 |  | 0
338 | [6 empty] | 0 |  | 0
339 | Deduct ( Base Set ) | [5 empty] | 0 |  | 0
340 | Chiller 1, 2 | [5 empty] | 0 |  | 0
341 | Disconnect Switch - 250A | 1364.6742 | EA |  |  | -2 | -2729.3485 |  | 0
342 | MDB to Chiller - 2"EMT - 3#3/0, 1#4 | [5 empty] | 0 |  | 0
343 | 2"EMT | 20.3622 | LF |  |  | -300 | -6108.6595 |  | 0
344 | #3/0 | 9.0912 | LF |  |  | -900 | -8182.1243 |  | 0
345 | #4 | 3.5374 | LF |  |  | -300 | -1061.235 |  | 0
346 | CHWP 1,2,3 | [5 empty] | 0 |  | 0
347 | 10HP - VFD Install Only | 1191.96 | EA |  |  | -3 | -3575.88 |  | 0
348 | 3/4"EMT - 4#12 - CHWP 1,3 to PPHB | [5 empty] | 0 |  | 0
349 | 3/4"EMT | 11.3784 | LF |  |  | -60 | -682.7067 |  | 0
350 | #12 | 1.1849 | LF |  |  | -240 | -284.3676 |  | 0
351 | 3/4"EMT - 4#10 - CHWP 2 to PPHB | [5 empty] | 0 |  | 0
352 | 3/4"EMT | 11.3784 | LF |  |  | -30 | -341.3533 |  | 0
353 | #12 | 1.1849 | LF |  |  | -120 | -142.1838 |  | 0
354 | AHU 1,2,3 | [5 empty] | 0 |  | 0
355 | PPAH-1,2,,3 ( Panels for AHU ) - 100A | 3984.925 | EA |  |  | -3 | -11954.775 |  | 0
356 | PPH3 to PP-AH1,2,3 - 3#2, #8 - 1-1/2"EMT | [5 empty] | 0 |  | 0
357 | 1-1/2"EMT | 17.9065 | LF |  |  | -350 | -6267.2715 |  | 0
358 | #2 | 4.5399 | LF |  |  | -1050 | -4766.8492 |  | 0
359 | #8 | 2.1136 | LF |  |  | -350 | -739.7602 |  | 0
360 | 7.5HP VFD - Install Only | 1191.96 | EA |  |  | -6 | -7151.76 |  | 0
361 | AHU1,2,3 to 7.5HP VFD - 3/4"EMT - 4#12 | [5 empty] | 0 |  | 0
362 | 3/4"EMT | 11.3784 | LF |  |  | -65 | -739.5989 |  | 0
363 | #12 | 1.1849 | LF |  |  | -260 | -308.0649 |  | 0
364 | 15HP VFD - Install Only | 1489.95 | EA |  |  | -6 | -8939.7 |  | 0
365 | AHU1,2,3 to 15HP VFD - 3/4"EMT - 4#10 | [5 empty] | 0 |  | 0
366 | 3/4"EMT | 11.3784 | LF |  |  | -150 | -1706.7667 |  | 0
367 | #10 | 1.5861 | LF |  |  | -600 | -951.633 |  | 0
368 | Junction Box - Heat Exchanger | 65.0482 | EA |  |  | -4 | -260.193 |  | 0
369 | 3/4"EMT | 11.3784 | LF |  |  | -80 | -910.2756 |  | 0
370 | #12 | 1.1849 | LF |  |  | -320 | -379.1568 |  | 0
371 | [6 empty] | 0 |  | 0
372 | Add ( Option 3 Criteria ) | [7 empty] | 0
373 | DOAS ( In Roof ) | [7 empty] | 0
374 | Disconnect Switch - 125A - Allow | 1000 | EA |  |  |  |  | 1 | 1000
375 | MDB to DOAS - 1-1/2"EMT - 4#1, 1#6 | [7 empty] | 0
376 | 1-1/2"EMT | 17.9065 | LF |  |  |  |  | 225 | 4028.9603
377 | #1 | 5.3408 | LF |  |  |  |  | 900 | 4806.749
378 | #6 | 2.7257 | LF |  |  |  |  | 225 | 613.2738
379 | Chiller ( In Roof ) | [7 empty] | 0
380 | Disconnect Switch - 250A | 2500 | EA |  |  |  |  | 1 | 2500
381 | MDB to Chiller -2-1/2"EMT - 3#350MCM, #3 | [7 empty] | 0
382 | 2-1/2"EMT | 27.93 | LF |  |  |  |  | 190 | 5306.7
383 | #350MCM | 15.5 | LF |  |  |  |  | 570 | 8835
384 | #3 | 3.95 | LF |  |  |  |  | 190 | 750.5
385 | CHWP 1,2 ( Allow 2 Pumps ) | [7 empty] | 0
386 | 10HP - VFD Install Only | 1191.96 | EA |  |  |  |  | 2 | 2383.92
387 | 3/4"EMT - 4#12 - CHWP 1,2 to PPHB | [7 empty] | 0
388 | 3/4"EMT | 11.3784 | LF |  |  |  |  | 55 | 625.8145
389 | #12 | 1.1849 | LF |  |  |  |  | 220 | 260.6703
390 | Junction Box - Heat Pumps | 65.0482 | EA |  |  |  |  | 51 | 3317.4607
391 | 3/4"EMT | 11.3784 | LF |  |  |  |  | 765 | 8704.5104
392 | #12 | 1.1849 | LF |  |  |  |  | 2295 | 2719.2652
393 | [8 empty] | 0
394 | Deduct ( Base Set ) | [7 empty] | 0
395 | Chiller 1, 2 | [7 empty] | 0
396 | Disconnect Switch - 250A | 1364.6742 | EA |  |  |  |  | -2 | -2729.3485
397 | MDB to Chiller - 2"EMT - 3#3/0, 1#4 | [7 empty] | 0
398 | 2"EMT | 20.3622 | LF |  |  |  |  | -300 | -6108.6595
399 | #3/0 | 9.0912 | LF |  |  |  |  | -900 | -8182.1243
400 | #4 | 3.5374 | LF |  |  |  |  | -300 | -1061.235
401 | CHWP 1,2,3 | [7 empty] | 0
402 | 10HP - VFD Install Only | 1191.96 | EA |  |  |  |  | -3 | -3575.88
403 | 3/4"EMT - 4#12 - CHWP 1,3 to PPHB | [7 empty] | 0
404 | 3/4"EMT | 11.3784 | LF |  |  |  |  | -60 | -682.7067
405 | #12 | 1.1849 | LF |  |  |  |  | -240 | -284.3676
406 | 3/4"EMT - 4#10 - CHWP 2 to PPHB | [7 empty] | 0
407 | 3/4"EMT | 11.3784 | LF |  |  |  |  | -30 | -341.3533
408 | #12 | 1.1849 | LF |  |  |  |  | -120 | -142.1838
409 | AHU 1,2,3 | [7 empty] | 0
410 | PPAH-1,2,,3 ( Panels for AHU ) - 100A | 3984.925 | EA |  |  |  |  | -3 | -11954.775
411 | PPH3 to PP-AH1,2,3 - 3#2, #8 - 1-1/2"EMT | [7 empty] | 0
412 | 1-1/2"EMT | 17.9065 | LF |  |  |  |  | -350 | -6267.2715
413 | #2 | 4.5399 | LF |  |  |  |  | -1050 | -4766.8492
414 | #8 | 2.1136 | LF |  |  |  |  | -350 | -739.7602
415 | 7.5HP VFD - Install Only | 1191.96 | EA |  |  |  |  | -6 | -7151.76
416 | AHU1,2,3 to 7.5HP VFD - 3/4"EMT - 4#12 | [7 empty] | 0
417 | 3/4"EMT | 11.3784 | LF |  |  |  |  | -65 | -739.5989
418 | #12 | 1.1849 | LF |  |  |  |  | -260 | -308.0649
419 | 15HP VFD - Install Only | 1489.95 | EA |  |  |  |  | -6 | -8939.7
420 | AHU1,2,3 to 15HP VFD - 3/4"EMT - 4#10 | [7 empty] | 0
421 | 3/4"EMT | 11.3784 | LF |  |  |  |  | -150 | -1706.7667
422 | #10 | 1.5861 | LF |  |  |  |  | -600 | -951.633
423 | Junction Box - Heat Exchanger | 65.0482 | EA |  |  |  |  | -4 | -260.193
424 | 3/4"EMT | 11.3784 | LF |  |  |  |  | -80 | -910.2756
425 | #12 | 1.1849 | LF |  |  |  |  | -320 | -379.1568
426 | Junction Box - VAV | 65.0482 | EA |  |  |  |  | -68 | -4423.281
427 | 3/4"EMT | 11.3784 | LF |  |  |  |  | -1020 | -11606.0139
428 | #12 | 1.1849 | LF |  |  |  |  | -3060 | -3625.6869
429 | [8 empty] | 0
430 | Power and lighting revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north
431
432 | Electrical & AV | 51.25 | SF | 49847 | 2554658.75 | 48567 | 2489058.75 | 48567 | 2489058.75
433 |  |  |  |  | - |  | - |  | -
434 | Subtotal 26-00-00 Electrical |  |  |  | 2539348.4015 |  | 2476522.4953 |  | 2447072.9288
435
436 | 27-00-00 Communications
437
438 | Telecom revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north
439
440 | Telecom | 3.39 | SF | 49847 | 168981.33 | 48567 | 164642.13 | 48567 | 164642.13
441 |  |  |  |  | - |  | - |  | -
442 | Subtotal 27-00-00 Communications |  |  |  | 168981.33 |  | 164642.13 |  | 164642.13
443
444 | 28-00-00 Electronic Safety & Security
445
446 | Electronic Safety and Security revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north
447
448 | Fire Alarm & Security | 8.69 | SF | 49847 | 433170.43 | 48567 | 422047.23 | 48567 | 422047.23
449 |  |  |  |  | - |  | - |  | -
450 | Subtotal 28-00-00 Electronic Safety & Security |  |  |  | 433170.43 |  | 422047.23 |  | 422047.23
451
452
453 | 31-00-00 Earthwork
454 | Structural revisions based on reducing Basement area by 1,400 square feet at south and 460 square feet at north | [8 empty] | GM
455
456 | DEDUCT
457 | Mass cut earth at reduced basement and areaway and stockpile for reuse | 21.5 | TON | 0 | 0 | -1102.2222 | -23697.7778 | -1102.2222 | -23697.7778 | GM
459 | Reuse earth backfill at reduced basement and areaway | 21.5 | TON | 0 | 0 | -1102.2222 | -23697.7778 | -1102.2222 | -23697.7778 | GM
461 | Pro rata share of pumping allowance during construction | 1 | LS | 0 | 0 | -2000 | -2000 | -2000 | -2000 | GM
462
463 |  |  |  |  | - |  | - |  | -
464 | Subtotal 31-00-00 Earthwork |  |  |  | 0 |  | -49395.5556 |  | -49395.5556
465
466 | 32-00-00 Exterior Improvements
467
468 |  |  |  |  | - |  | - |  | -
469 | Subtotal 32-00-00 Exterior Improvements |  |  |  | 0 |  | 0 |  | 0
470
471 | 33-00-00 Utilities
472
473 | DEDUCT
474
475 | Credit for Deletion of on site Cooling Tower slab and enclosure for Options 1, 2 & 3
476
477 | Cooling Tower Enclosure and Dunnage | [8 empty] | GM
478 | 6" crushed stone gravel paving at cooling tower - includes 6" mow strip around outside | 10.75 | SF | -1100 | -11825 | -1100 | -11825 | -1100 | -11825 | GM
479 | 6'W x 1.5' D continuous wall footing for the 12" thick block wall enclosure for cooling tower | 1006.2 | CY | -47 | -47291.4 | -47 | -47291.4 | -47 | -47291.4 | GM
480 | Concrete Footing for cooling towers support columns and reinforced concrete pedestal for cooling tower support framing | 1107.25 | CY | -3 | -3321.75 | -3 | -3321.75 | -3 | -3321.75 | GM
481 | Galvanized steel support framing for cooling tower | 3.354 | LBS | -2973 | -9971.442 | -2973 | -9971.442 | -2973 | -9971.442 | GM
482 | 12" thick CMU block wall with grout infill and #7 rebar - 18' H x 140 LF | 43 | SF | -2520 | -108360 | -2520 | -108360 | -2520 | -108360 | GM
483 | 4" CMU filled solid with concrete on the outter side of the wall on the footing - 2' H x 145 LF | 16.125 | SF | -290 | -4676.25 | -290 | -4676.25 | -290 | -4676.25 | GM
484 | 6" Concrete Slab on additional 6" crushed Stone Footing | 11.825 | SF | -40 | -473 | -40 | -473 | -40 | -473 | GM
485 | 10" Concrete Slab on additional 6" crushed Stone Footing - 4 SF | 268.75 | EA | -1 | -268.75 | -1 | -268.75 | -1 | -268.75 | GM
486 |  |  |  |  | 0 |  | 0 |  | 0 | GM
487 | Ext-11 - Cooling tower door - Double leaves of 4' x 8'6" door, hollow metal insulated 1 3/4" thick, painted, complete with SC/EXT threshold including hardware | 3988.25 | EA | -1 | -3988.25 | -1 | -3988.25 | -1 | -3988.25 | GM
488 | Enclosure |  |  |  | 0 |  | 0 |  | 0 | GM
489 | Aluminum Composite Panels to Cooling Tower Enclosure | 53.75 | SF | -2549 | -137008.75 | -2549 | -137008.75 | -2549 | -137008.75 | GM
490 | Extra-over for Aluminum Composite Panel coping | 53.75 | LF | -146 | -7847.5 | -146 | -7847.5 | -146 | -7847.5 | GM
491 | Extra-over for SS flashing | 53.75 | LF | -146 | -7847.5 | -146 | -7847.5 | -146 | -7847.5 | GM
492
493 | Landscaping
494 | Additional cost for landscaping | 25 | SF | 1230 | 30750 | 1230 | 30750 | 1230 | 30750 | GM
495 |  |  |  |  | 0
496 | Geothermal |  |  |  | 0
497 | Geothermal loop, boring, piping | 1075000 | EA | 1 | 1075000 |  | 0 | 0 | 0
498 | Geothermal loop from building to geothermal field | 9600 | LOC | 48 | 460800 |  | 0 | 0 | 0
499 |  |  |  |  | 0 |  | 0 |  | 0
500 | Cooling Tower -Electrical |  |  |  | 0 |  | 0 |  | 0
501 | Site |  |  |  | 0 |  | 0 |  | 0
502 | Outside Building Connection - MDP to PPHC - 2"PVC - 4#1, 1#8 |  |  |  | 0 |  | 0 |  | 0
503 | 2"PVC | 16.4849 | LF | -120 | -1978.1931 | -120 | -1978.1931 | -120 | -1978.1931
504 | #1 | 5.3408 | LF | -480 | -2563.5995 | -480 | -2563.5995 | -480 | -2563.5995
505 | #8 | 2.1136 | LF | -120 | -253.6321 | -120 | -253.6321 | -120 | -253.6321
506 | Concrete | 565.9875 | CY | -1.1111 | -628.875 | -1.1111 | -628.875 | -1.1111 | -628.875
507 | Excavation & Backfill | 104.2965 | CY | -3.3333 | -347.655 | -3.3333 | -347.655 | -3.3333 | -347.655
508 | Building |  |  |  | 0 |  | 0 |  | 0
509 | Inside Building Connection - MDP to PPHC - 2"EMT - 4#1, 1#8 |  |  |  | 0 |  | 0 |  | 0
510 | 2"EMT | 20.3622 | LF | -140 | -2850.7078 | -140 | -2850.7078 | -140 | -2850.7078
511 | #1 | 5.3408 | LF | -560 | -2990.866 | -560 | -2990.866 | -560 | -2990.866
512 | #8 | 2.1136 | LF | -140 | -295.9041 | -140 | -295.9041 | -140 | -295.9041
513 | Connections & Devices - Inside Cooling Tower |  |  |  | 0 |  | 0 |  | 0
514 | PPHC Panel 100A - 3Ph, 4 W - 277/480V | 3984.925 | EA | -1 | -3984.925 | -1 | -3984.925 | -1 | -3984.925
515 | MPZ Panel - 60A - 3Ph, 4W - 120/208V | 2450 | EA | -1 | -2450 | -1 | -2450 | -1 | -2450
516 | PPHC to MPZ - 3#8, 1#10 - 3/4"EMT |  |  |  | 0 |  | 0 |  | 0
517 | 3/4"EMT | 11.3784 | LF | -10 | -113.7844 | -10 | -113.7844 | -10 | -113.7844
518 | #8 | 2.1136 | LF | -30 | -63.408 | -30 | -63.408 | -30 | -63.408
519 | #10 | 1.5861 | LF | -10 | -15.8605 | -10 | -15.8605 | -10 | -15.8605
520 | Wiring Devices |  |  |  | 0 |  | 0 |  | 0
521 | Duplex Receptacle GFI - WP | 144.996 | EA | -2 | -289.992 | -2 | -289.992 | -2 | -289.992
522 | 3/4"RGS | 19.9698 | LF | -30 | -599.0934 | -30 | -599.0934 | -30 | -599.0934
523 | #12 | 1.1849 | LF | -90 | -106.6378 | -90 | -106.6378 | -90 | -106.6378
524 | Mechanical Equipment Devices |  |  |  | 0 |  | 0 |  | 0
525 | 3HP VFD- Install Only - WP - CT- 1,2 | 993.3 | EA | -2 | -1986.6 | -2 | -1986.6 | -2 | -1986.6
526 | 1"RGS | 27.25 | LF | -40 | -1090 | -40 | -1090 | -40 | -1090
527 | #12 | 1.1849 | LF | -160 | -189.5784 | -160 | -189.5784 | -160 | -189.5784
528 | Junction Box - WP - 3/4"RGS - 3#12 | 77.9483 | EA | -1 | -77.9483 | -1 | -77.9483 | -1 | -77.9483
529 | 3/4"RGS | 19.9698 | LF | -15 | -299.5467 | -15 | -299.5467 | -15 | -299.5467
530 | #12 | 1.1849 | LF | -45 | -53.3189 | -45 | -53.3189 | -45 | -53.3189
531 | Motor Starter w/ Disconnect 30A - WP - 1"RGS - 4#12 | 701.651 | EA | -1 | -701.651 | -1 | -701.651 | -1 | -701.651
532 | 1"RGS | 27.25 | LF | -20 | -545 | -20 | -545 | -20 | -545
533 | #12 | 1.1849 | LF | -80 | -94.7892 | -80 | -94.7892 | -80 | -94.7892
534 | Site Lighting |  |  |  | 0 |  | 0 |  | 0
535 | FX2 | 77.9483 | EA | -4 | -311.793 | -4 | -311.793 | -4 | -311.793
536 | 1"PVC | 11.5535 | LF | -60 | -693.2099 | -60 | -693.2099 | -60 | -693.2099
537 | #12 | 1.1849 | LF | -180 | -213.2757 | -180 | -213.2757 | -180 | -213.2757
538 | Concrete | 565.9875 | CY | -1 | -565.9875 | -1 | -565.9875 | -1 | -565.9875
539 | Excavation & Backfill | 104.2965 | CY | -3 | -312.8895 | -3 | -312.8895 | -3 | -312.8895
540 |  |  |  |  | 0 |  | 0 |  | 0
541 |  |  |  |  | - |  | - |  | -
542 | Subtotal 33-00-00 Utilities |  |  |  | 1197001.6862 |  | -338798.3138 |  | -338798.3138
543
The End
[5 empty] | 28594817.9525 |  | 26347019.1004 |  | 25205527.2803
[5 empty] | 28594817.9525 |  | 26347019.1004 |  | 25205527.2803

## SUM SITE
| COLLEGE OF TECHNOLOGY AT FARMINGDALE |  |  |  | 2021-03-08
NET ZERO CARBON STUDY
Concept Estimate
SUMMARY OF TRADES-SITE
| Description |  | Material | Labor | Total
1 | 01-00-00 General Requirements |  | 303540.9463 | 404744.192 | 708285.1383
2 | 02-00-01 Site Clearing |  | 181844.506 | 487937.684 | 669782.19 |  |  |  | 3.0212
3 | 02-00-02 Earthwork |  | 210524.56 | 790635.84 | 1001160.4 |  |  |  | 4.5159
4 | 02-00-03 Pavements |  | 931689.299 | 770566.2135 | 1702255.5125 |  |  |  | 7.6784
5 | 02-00-04 Site Features |  | 400253.2585 | 588787.0447 | 989040.3032 |  |  |  | 4.4613
6 | 02-00-05 Concrete Walks |  | 0 | 0 | 0 |  |  |  | 0
7 | 02-00-06 Utilities-Plumbing |  | 642827.726 | 595424.7087 | 1238252.4348 |  |  |  | 5.5854
8 | 02-00-07 Utilities- Heating/Cooling |  | 0 | 0 | 0 |  |  |  | 0
9 | 02-00-08 Utilities- Electrical |  | 519224.4381 | 537019.3056 | 1056243.7437 |  |  |  | 4.7644
10 | 02-00-09 Planting |  | 128081.2405 | 193213.3835 | 321294.624 |  |  |  | 1.4493
11 | 02-00-10 Abatement |  | 20964.435 | 83857.74 | 104822.175 |  |  |  | 0.47282
12 |  |  | - | - | -
13 | Subtotal 1 |  | 3338950.4094 | 4452186.1121 | 7791136.5215 |  | 7082851.3832
14 | General Contractor's Office Overhead & Profit | 8% | 267116.0328 | 356174.889 | 623290.9217
15 |  |  | - | - | -
16 | Subtotal 2 |  | 3606066.4422 | 4808361.001 | 8414427.4432
17 | Design Contingency | 0% | 0 | 0 | 0
18 |  |  | - | - | -
19 | Subtotal 3 |  | 3606066.4422 | 4808361.001 | 8414427.4432
20 | Escalation to (Midpoint of Construction) | 8.438% | 304261.8561 | 405705.4595 | 709967.3155
21 |  |  | - | - | -
22 | Total CONSTRUCTION Cost |  | 3910328.2982 | 5214066.4605 | 9124394.7587
23 | Bid Contingency | 5% | 195516.4149 | 260703.323 | 456219.7379 |  |  | 1.3721
24 |  |  | - | - | -
25 | Total CONSTRUCTION Cost w/Bid Contingency |  | 4105844.7131 | 5474769.7835 | 9580614.4967 | 1.2297 | 0.13526
| Total Gross Area in SF | 221695
| Construction Cost per GSF |  | 17.6383 | 23.5191 | 41.1574
| Cost per GSF w/Bid Contingency |  | 18.5202 | 24.6951 | 43.2153

## EST SITE
COLLEGE OF TECHNOLOGY AT FARMINGDALE
Farmingdale, New York
| Concept Estimate | [7 empty] | 2021-03-08 | 7.5
| NET ZERO CARBON STUDY | [8 empty] | 1.075 | 1.075
PREVIOUS ESTIMATE
| Description | Quantity | Unit | Material |  | Labor |  | Total | Amount | Material | Labor
|  |  |  | Unit | Amount | Unit | Amount | Unit | Amount | Unit | Unit
1
2 | 01-00-00 General Requirements
3
4 | Site General Conditions - 10% | 1 | LS | 303540.9463 | 303540.9463 | 404744.192 | 404744.192 | 708285.1383 | 708285.1383
5 |  |  |  |  | - |  | - |  | -
6 | Subtotal 01-00-00 General Requirements |  |  |  | 303540.9463 |  | 404744.192 |  | 708285.1383
7
8 | 02-00-01 Site Clearing
9
10 | Construct and maintain 8' high construction fence and wind screen - 3,130 LF | 25040 | SF | 5.9125 | 148049 | 10.2125 | 255721 | 16.125 | 403770 | 5.5 | 9.5
11 |  |  |  |  | 0 |  | 0
12 | Clear and grub site as required - original | 59736 | SF | 0.086 | 5137.296 | 0.129 | 7705.944 | 0.215 | 12843.24 | 0.08 | 0.12
13 | Fine grading: |  |  |  | 0 |  | 0
14 | Fine grading to achieve subgrade levels of pavements across site | 59736 | SF | 0.1075 | 6421.62 | 0.16125 | 9632.43 | 0.26875 | 16054.05 | 0.1 | 0.15
15 |  |  |  |  | 0 |  | 0
16 | Soft landscaping: |  |  |  | 0 |  | 0
17 | Protect trees | 10 | EA | 134.375 | 1343.75 | 403.125 | 4031.25 | 537.5 | 5375 | 125 | 375
18 | Remove trees - 0" - 8" | 5 | EA |  | 0 | 553.625 | 2768.125 | 553.625 | 2768.125 | 0 | 515
19 | Remove trees - 8"-35" | 15 | EA |  | 0 | 806.25 | 12093.75 | 806.25 | 12093.75 | 0 | 750
20 | Remove trees >35" | 2 | EA |  | 0 | 1612.5 | 3225 | 1612.5 | 3225 | 0 | 1500
21 | Remove trees - sizing not specified | 5 | EA |  | 0 | 1612.5 | 8062.5 | 1612.5 | 8062.5 | 0 | 1500
22 |  |  |  |  | 0 |  | 0
23 | Hard landscaping: |  |  |  | 0 |  | 0
24 | Remove existing bench | 10 | LF |  | 0 | 215 | 2150 | 215 | 2150 | 0 | 200
25 | Remove existing curb | 195 | LF |  | 0 | 16.125 | 3144.375 | 16.125 | 3144.375 | 0 | 15
26 | Remove existing retaining wall | 139 | LF |  | 0 | 107.5 | 14942.5 | 107.5 | 14942.5 | 0 | 100
27 | Remove pavement | 2451 | SF |  | 0 | 2.6875 | 6587.0625 | 2.6875 | 6587.0625 | 0 | 2.5
28 | Remove sign | 3 | EA |  | 0 | 107.5 | 322.5 | 107.5 | 322.5 | 0 | 100
29 | Sawcut Pavement | 554 | LF |  | 0 | 10.75 | 5955.5 | 10.75 | 5955.5 | 0 | 10
30 |  |  |  |  | 0 |  | 0
31 | Works within C-101 paths (Grey) area: |  |  |  | 0 |  | 0
32 | Remove concrete pavement, curb & bitumen | 24985 | SF |  | 0 | 2.6875 | 67147.1875 | 2.6875 | 67147.1875 | 0 | 2.5
33 | Extra-over removal of concrete pavement for removal of existing curb | 310 | LF |  | 0 | 16.125 | 4998.75 | 16.125 | 4998.75 | 0 | 15
34 | Remove wood bench | 72 | LF |  | 0 | 26.875 | 1935 | 26.875 | 1935 | 0 | 25
35 | Remove sidewalk concrete walls | 161 | LF |  | 0 | 107.5 | 17307.5 | 107.5 | 17307.5 | 0 | 100
36 | Remove sidewalk masonry walls | 574 | LF |  | 0 | 80.625 | 46278.75 | 80.625 | 46278.75 | 0 | 75
37 | Car Park |  |  |  | 0 |  | 0
38 | Site clearing: |  |  |  | 0 |  | 0
39 | Clear and grub site as required - parking | 161960 | SF | 0.129 | 20892.84 | 0.086 | 13928.56 | 0.215 | 34821.4 | 0.12 | 0.08
40 |  |  |  |  | 0 | 0 | 0
41 |  |  |  |  | - | 0 | - |  | -
42 | Subtotal 02-00-01 Site Clearing |  |  |  | 181844.506 | 0 | 487937.684 |  | 669782.19
43 | [5 empty] | 0
44 | 02-00-02 Earthwork |  |  |  |  | 0
45 | [5 empty] | 0
46 | Mass cut earth at south side of basement and basement areaways | 5928 | CY |  | 0 | 21.5 | 127452 | 21.5 | 127452 | 0 | 20
47 |  |  |  |  | 0 |  | 0
48 | Mass cut earth at first floor for SOG | 444 | CY |  | 0 | 21.5 | 9546 | 21.5 | 9546 | 0 | 20
49 |  |  |  |  | 0 |  | 0
50 | Overcut on the north side of the building for foundation walls - 260LF x 15.25 avg. deep ( step cut) on side ( 1766 SF) | 1014 | CY |  | 0 | 21.5 | 21801 | 21.5 | 21801 | 0 | 20
51 | Overcut excavation for areas beyond the above cut area - 9,140 SF x 10' avg. depth | 3385 | CY |  | 0 | 21.5 | 72777.5 | 21.5 | 72777.5 | 0 | 20
52 |  |  |  |  | 0 |  | 0
53 | Isolated excavation for footings/ pits at cellar level foundation only | 508 | CY |  | 0 | 26.875 | 13652.5 | 26.875 | 13652.5 | 0 | 25
54 |  |  |  |  | 0 |  | 0
55 | Reuse earth backfill | 4362 | CY |  | 0 | 21.5 | 93783 | 21.5 | 93783 | 0 | 20
56 |  |  |  |  | 0 |  | 0
57 | Disposal of excess earth cut off site | 6918 | CY |  | 0 | 21.5 | 148737 | 21.5 | 148737 | 0 | 20
58 |  |  |  |  | 0 |  | 0
59 | Sheeting at basement and basement areaways at back of building only (Sinclair Building) - assume 20' Depth and 325' Length ( as per C-104) | 6500 | SF | 23.65 | 153725 | 35.475 | 230587.5 | 59.125 | 384312.5 | 22 | 33
60 |  |  |  |  | 0 |  | 0
61 | Pumping during construction | 3 | Monts | 6020 | 18060 | 4730 | 14190 | 10750 | 32250 | 5600 | 4400
62 |  |  |  |  | 0 |  | 0
63 | Site Grading |  |  |  | 0 |  | 0
64 | Cut/fill on site generally +- 2' deep | 33068 | SF | 0.645 | 21328.86 | 0.9675 | 31993.29 | 1.6125 | 53322.15 | 0.6 | 0.9
65 | Car Park |  |  |  | 0 |  | 0
66 | Minor spreading and levelling to carpark generally finished to exist. levels | 161960 | SF | 0.1075 | 17410.7 | 0.16125 | 26116.05 | 0.26875 | 43526.75 | 0.1 | 0.15
67 |  |  |  |  | - | 0 | - |  | - | 0 | 0
68 | Subtotal 02-00-02 Earthwork |  |  |  | 210524.56 | 0 | 790635.84 |  | 1001160.4 | 0 | 0
69 | [5 empty] | 0 |  |  |  | 0 | 0
70 | 02-00-03 Pavements |  |  |  |  | 0 |  |  |  | 0 | 0
71 | [5 empty] | 0 |  |  |  | 0 | 0
72 | P1: Concrete Sidewalk with brick border
73 | Compact subgrade & place 6" RCA fill | 3706 | SF | 0.645 | 2390.37 | 0.9675 | 3585.555 | 1.6125 | 5975.925 | 0.6 | 0.9
74 | Decorative 8" concrete pavement w/ in situ sawcut joints, 6 x 6 x 10" Wire Mesh | 3706 | SF | 5.375 | 19919.75 | 8.0625 | 29879.625 | 13.4375 | 49799.375 | 5 | 7.5
75 | Extra-over P1 for 3 unit concrete paver bands, sand blinding & edge restraint | 319 | LF | 8.6 | 2743.4 | 12.9 | 4115.1 | 21.5 | 6858.5 | 8 | 12
76 | P2: Concrete Sidewalk Standard |  |  |  | 0 |  | 0
77 | Compact subgrade, lay woven geotextile & place 6" clean stone | 6386 | SF | 0.43 | 2745.98 | 0.645 | 4118.97 | 1.075 | 6864.95 | 0.4 | 0.6
78 | 8" thk 4000 PSI w/ 6 x 6 x 10/10 Wire Mesh | 6386 | SF | 9.03 | 57665.58 | 4.945 | 31578.77 | 13.975 | 89244.35 | 8.4 | 4.6
79 | P3: Concrete Plank Paver |  |  |  | 0 |  | 0
80 | P3.1: Compact subgrade, place 8" compacted dense graded aggregate base | 1891 | SF | 1.075 | 2032.825 | 1.6125 | 3049.2375 | 2.6875 | 5082.0625 | 1 | 1.5
81 | P3.1: 6" concrete base w/ 6 x 6 x 10 wire mesh, 3/4" sand bed & concrete unit plank pavers | 1891 | SF | 15.05 | 28459.55 | 22.575 | 42689.325 | 37.625 | 71148.875 | 14 | 21
82 | P3.2: Place 2'0" certified structural soil on uncompacted subgrade | 1547 | SF | 3.87 | 5986.89 | 2.58 | 3991.26 | 6.45 | 9978.15 | 3.6 | 2.4
83 | P3.2: Concrete unit plank pavers only | 1547 | SF | 17.587 | 27207.089 | 12.513 | 19357.611 | 30.1 | 46564.7 | 16.36 | 11.64
84 | Edging: |  |  |  | 0 |  | 0
85 | 2" thick 1' wide Bluestone edging on 4" Compacted crushed stone, 1" stone dust | 310 | LF | 32.25 | 9997.5 | 21.5 | 6665 | 53.75 | 16662.5 | 30 | 20
86 | Cast stone base on epoxy to perimeter of cooling tower | 146 | LF | 30.96 | 4520.16 | 38.915 | 5681.59 | 69.875 | 10201.75 | 28.8 | 36.2
87 | Car Park |  |  |  | 0 |  | 0
88 | Asphalt Pavement |  |  |  | 0 |  | 0
89 | Compacted subgrade and lay Mirafi 500X or equal geotextile fabric, 12" compacted granular basecourse | 114562 | SF | 1.075 | 123154.15 | 1.6125 | 184731.225 | 2.6875 | 307885.375 | 1 | 1.5
90 | Lay 4" bituminous concrete basecourse, 3" binder course and 1" bituminous conc wearing course | 114562 | SF | 4.1925 | 480301.185 | 2.2575 | 258623.715 | 6.45 | 738924.9 | 3.9 | 2.1
91 | Supply and install curbs to carpark | 3363 | LF | 11.61 | 39044.43 | 7.74 | 26029.62 | 19.35 | 65074.05 | 10.8 | 7.2
92 | Raised concrete pavement to carpark | 3321 | SF | 8.6 | 28560.6 | 12.9 | 42840.9 | 21.5 | 71401.5 | 8 | 12
93 | P2: Concrete Sidewalk Standard |  |  |  | 0 |  | 0
94 | Compact subgrade, lay woven geotextile & place 6" clean stone | 5368 | SF | 0.43 | 2308.24 | 0.645 | 3462.36 | 1.075 | 5770.6 | 0.4 | 0.6
95 | 8" thk 4000 PSI w/ 6 x 6 x 10/10 Wire Mesh | 5368 | SF | 9.03 | 48473.04 | 4.945 | 26544.76 | 13.975 | 75017.8 | 8.4 | 4.6
96 | Line marking |  |  |  | 0 |  | 0
97 | Parking diagonal striping | 3796 | SF | 0.86 | 3264.56 | 1.29 | 4896.84 | 2.15 | 8161.4 | 0.8 | 1.2
98 | Zebra Crossing | 97 | SF | 21.5 | 2085.5 | 32.25 | 3128.25 | 53.75 | 5213.75 | 20 | 30
99 | Parking alignment striping - per space | 290 | EA | 129 | 37410 | 193.5 | 56115 | 322.5 | 93525 | 120 | 180
100 | Extra-over for wheelchair painting | 8 | EA | 64.5 | 516 | 96.75 | 774 | 161.25 | 1290 | 60 | 90
101 |  |  |  |  | 0 |  | 0
102 | Concrete ramp and footings at the rear entrance at south of building | 270 | SF | 10.75 | 2902.5 | 32.25 | 8707.5 | 43 | 11610 | 10 | 30
103 |  |  |  |  | - | 0 | - |  | - | 0 | 0
104 | Subtotal 02-00-03 Pavements |  |  |  | 931689.299 | 0 | 770566.2135 |  | 1702255.5125 | 0 | 0
105 | [5 empty] | 0 |  |  |  | 0 | 0
106 | 02-00-04 Site Features |  |  |  |  | 0 |  |  |  | 0 | 0
107 | [5 empty] | 0 |  |  |  | 0 | 0
108 | Cooling Tower Enclosure and Dunnage
109 | 6" crushed stone gravel paving at cooling tower - includes 6" mow strip around outside | 1100 | SF | 4.3 | 4730 | 6.45 | 7095 | 10.75 | 11825 | 4 | 6
110 | 6'W x 1.5' D continuous wall footing for the 12" thick block wall enclosure for cooling tower | 46.6111 | CY | 402.48 | 18760.04 | 603.72 | 28140.06 | 1006.2 | 46900.1 | 374.4 | 561.6
111 | Concrete Footing for cooling towers support columns and reinforced concrete pedestal for cooling tower support framing | 3.23 | CY | 442.728 | 1430.0114 | 664.092 | 2145.0172 | 1106.82 | 3575.0286 | 411.84 | 617.76
112 | Galvanized steel support framing for cooling tower | 2973 | LBS | 1.3416 | 3988.5768 | 2.0124 | 5982.8652 | 3.354 | 9971.442 | 1.248 | 1.872
113 | 12" thick CMU block wall with grout infill and #7 rebar - 18' H x 140 LF | 2520 | SF | 10.75 | 27090 | 32.25 | 81270 | 43 | 108360 | 10 | 30
114 | 4" CMU filled solid with concrete on the outter side of the wall on the footing - 2' H x 145 LF | 290 | SF | 4.0312 | 1169.0625 | 12.0938 | 3507.1875 | 16.125 | 4676.25 | 3.75 | 11.25
115 | 6" Concrete Slab on additional 6" crushed Stone Footing | 40.33 | SF | 4.73 | 190.7609 | 7.095 | 286.1413 | 11.825 | 476.9022 | 4.4 | 6.6
116 | 10" Concrete Slab on additional 6" crushed Stone Footing - 4 SF | 1 | EA | 67.1875 | 67.1875 | 201.5625 | 201.5625 | 268.75 | 268.75 | 62.5 | 187.5
117 |  |  |  |  | 0 |  | 0
118 | Ext-11 - Cooling tower door - Double leaves of 4' x 8'6" door, hollow metal insulated 1 3/4" thick, painted, complete with SC/EXT threshold including hardware | 1 | EA | 1982.3 | 1982.3 | 2005.95 | 2005.95 | 3988.25 | 3988.25 | 1844 | 1866
119 | Enclosure |  |  |  | 0 |  | 0
120 | Aluminum Composite Panels to Cooling Tower Enclosure | 2549 | SF | 28.9444 | 73779.4 | 24.8056 | 63229.35 | 53.75 | 137008.75 | 26.9251 | 23.0749
121 | Extra-over for Aluminum Composite Panel coping | 146 | LF | 36.55 | 5336.3 | 17.2 | 2511.2 | 53.75 | 7847.5 | 34 | 16
122 | Extra-over for SS flashing | 146 | LF | 32.25 | 4708.5 | 21.5 | 3139 | 53.75 | 7847.5 | 30 | 20
123 |  |  |  |  | 0 |  | 0
124 | Concrete pad | 28 | SF | 4.73 | 132.44 | 7.095 | 198.66 | 11.825 | 331.1 | 4.4 | 6.6
125 | Knee Wall up to frost Line for the 6" concrete pad outside the building ( 8" thick) - 20 LF | 1.9852 | CY | 402.48 | 798.9973 | 603.72 | 1198.496 | 1006.2 | 1997.4933 | 374.4 | 561.6
126 | 8" Lean Concrete Trench box for Utilities - 30LF long | 3.7222 | CY | 442.728 | 1647.932 | 603.72 | 2247.18 | 1046.448 | 3895.112 | 411.84 | 561.6
127 |  | ` |  |  | 0 |  | 0
128 | Building exterior entry stair including granite finish treads and risers, concrete footings and grade beams and all associated earthwork | 100 | LF | 107.5 | 10750 | 161.25 | 16125 | 268.75 | 26875 | 100 | 150
129 |  |  |  |  | 0 |  | 0
130 | Free standing railing at above entry stair and ramps | 82 | LF | 107.5 | 8815 | 161.25 | 13222.5 | 268.75 | 22037.5 | 100 | 150
131 |  |  |  |  | 0 |  | 0
132 | Walls |  |  |  | 0 |  | 0
133 | Brick faced retaining wall: |  |  |  | 0 |  | 0
134 | Excavation for footing | 281 | CY |  | 0 | 26.875 | 7551.875 | 26.875 | 7551.875 | 0 | 25
135 | Dispose off remaining earth | 210 | CY |  | 0 | 48.375 | 10158.75 | 48.375 | 10158.75 | 0 | 45
136 | Concrete for wall foundation w/ reinforcement and formwork | 210 | CY | 378.4 | 79464 | 440.75 | 92557.5 | 819.15 | 172021.5 | 352 | 410
137 | Compacted gravel | 58 | CY | 12.9 | 748.2 | 19.35 | 1122.3 | 32.25 | 1870.5 | 12 | 18
138 | Brick facing for the retaining wall | 1848 | SF | 6.45 | 11919.6 | 25.8 | 47678.4 | 32.25 | 59598 | 6 | 24
139 | 24" wide, 4" thick precast capstone | 616 | LF | 64.5 | 39732 | 123.625 | 76153 | 188.125 | 115885 | 60 | 115
140 |  |  |  |  | 0 |  | 0
141 | Fixtures |  |  |  | 0 |  | 0
142 | Precast Concrete Bench: |  |  |  | 0 |  | 0
143 | Granite bench 4' x 18" x 18" monolithic | 16 | EA | 1290 | 20640 | 860 | 13760 | 2150 | 34400 | 1200 | 800
144 | Extra over for 4" haunch to granite bench | 152 | LF | 8.6 | 1307.2 | 12.9 | 1960.8 | 21.5 | 3268 | 8 | 12
145 |  |  |  |  | 0 |  | 0
146 | Bike Racks |  |  |  | 0 |  | 0
147 | Surface mounted bike racks | 4 | EA | 645 | 2580 | 430 | 1720 | 1075 | 4300 | 600 | 400
148 |  |  |  |  | 0 |  | 0
149 | Carpark |  |  |  | 0 |  | 0
150 | Temporary Works |  |  |  | 0 |  | 0
151 | Build and maintain site staging area and rent construction trailers, fencing as required | 30 | MONTH | 286.6667 | 8600 | 430 | 12900 | 716.6667 | 21500 | 266.6667 | 400
152 | Silt fence | 3126 | LF | 10.75 | 33604.5 | 16.125 | 50406.75 | 26.875 | 84011.25 | 10 | 15
153 | Stabilized construction area 36 x 24 | 1 | EA | 2150 | 2150 | 3225 | 3225 | 5375 | 5375 | 2000 | 3000
154 | 2 x 12'0" Construction fence | 1 | EA | 2150 | 2150 | 3225 | 3225 | 5375 | 5375 | 2000 | 3000
155 | Inlet protection to catch basins | 21 | EA | 645 | 13545 | 967.5 | 20317.5 | 1612.5 | 33862.5 | 600 | 900
156 |  |  |  |  | 0 |  | 0
157 | Site Improvements |  |  |  | 0 |  | 0
158 | Signage: |  |  |  | 0 |  | 0
159 | Free Standing Site Building Signage | 1 | EA | 6235 | 6235 | 4515 | 4515 | 10750 | 10750 | 5800 | 4200
160 | Accessible parking space sign | 8 | EA | 483.75 | 3870 | 322.5 | 2580 | 806.25 | 6450 | 450 | 300
161 | No Parking Sign | 1 | EA | 483.75 | 483.75 | 322.5 | 322.5 | 806.25 | 806.25 | 450 | 300
162 | Reserved Parking Sign | 3 | EA | 483.75 | 1451.25 | 322.5 | 967.5 | 806.25 | 2418.75 | 450 | 300
163 | Stop Sign | 1 | EA | 483.75 | 483.75 | 322.5 | 322.5 | 806.25 | 806.25 | 450 | 300
164 | Fixtures: |  |  |  | 0 |  | 0
165 | Manual swing vehicle entry gate including footings | 1 | PR | 5912.5 | 5912.5 | 4837.5 | 4837.5 | 10750 | 10750 | 5500 | 4500
166 |  |  |  |  | - | 0 | - |  | - | 0 | 0
167 | Subtotal 02-00-04 Site Features |  |  |  | 400253.2585 | 0 | 588787.0447 |  | 989040.3032 | 0 | 0
168 | [5 empty] | 0 |  |  |  | 0 | 0
169 | 02-00-05 Concrete Walks |  |  |  |  | 0 |  |  | w/ 02-00-04 | 0 | 0
170 | [5 empty] | 0 |  |  |  | 0 | 0
171 |  |  |  |  | - | 0 | - |  | - | 0 | 0
172 | Subtotal 02-00-05 Concrete Walks |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
173 | [5 empty] | 0 |  |  |  | 0 | 0
174 | 02-00-06 Utilities-Plumbing |  |  |  |  | 0 |  |  |  | 0 | 0
175 | [5 empty] | 0 |  |  |  | 0 | 0
176 | Water Service
177 | Cut and cap existing water line | 1 | CONN |  | 0 | 5375 | 5375 | 5375 | 5375 | 0 | 5000
178 | Relocate existing water valve | 1 | EA |  | 0 | 1612.5 | 1612.5 | 1612.5 | 1612.5 | 0 | 1500
179 | Remove existing manholes | 2 | EA |  | 0 | 5375 | 10750 | 5375 | 10750 | 0 | 5000
180 | Remove existing water line | 121 | LF |  | 0 | 33.4647 | 4049.2347 | 33.4647 | 4049.2347 | 0 | 31.13
181 | Water valves - 8" | 5 | EA | 2451 | 12255 | 1634 | 8170 | 4085 | 20425 | 2280 | 1520
182 | New 12" water service piping - include all trenching and backfill | 439 | LF | 103.2 | 45304.8 | 68.8 | 30203.2 | 172 | 75508 | 96 | 64
183 | New 8" water service piping - include all trenching and backfill | 499 | LF | 88.365 | 44094.135 | 58.91 | 29396.09 | 147.275 | 73490.225 | 82.2 | 54.8
184 | New 3" domestic water piping - include all trenching and backfill | 42 | LF | 61.92 | 2600.64 | 41.28 | 1733.76 | 103.2 | 4334.4 | 57.6 | 38.4
185 | Connections to new building | 1 | EA | 3225 | 3225 | 2150 | 2150 | 5375 | 5375 | 3000 | 2000
186 | Fire Protection |  |  |  | 0 |  | 0
187 | Relocate fire hydrant | 2 | EA |  | 0 | 5375 | 10750 | 5375 | 10750 | 0 | 5000
188 | New 6" sprinkler service piping - include all trenching and backfill | 40 | LF | 68.8 | 2752 | 44.075 | 1763 | 112.875 | 4515 | 64 | 41
189 | New curb valve and box | 1 | EA | 537.5 | 537.5 | 1075 | 1075 | 1612.5 | 1612.5 | 500 | 1000
190 | Sanitary/ Sewer Service |  |  |  | 0 |  | 0
191 | Relocate sanitary manhole | 1 | EA |  | 0 | 5375 | 5375 | 5375 | 5375 | 0 | 5000
192 | Remove sewer line | 581 | LF |  | 0 | 55.9 | 32477.9 | 55.9 | 32477.9 | 0 | 52
193 | Seal manhole penetration | 1 | EA |  | 0 | 2687.5 | 2687.5 | 2687.5 | 2687.5 | 0 | 2500
194 | New 4" sewer service piping - include all trenching and backfill | 29 | LF | 70.305 | 2038.845 | 46.87 | 1359.23 | 117.175 | 3398.075 | 65.4 | 43.6
195 | Manholes (2 new with connections to 3 existing) | 3 | EA | 5318.025 | 15954.075 | 3545.35 | 10636.05 | 8863.375 | 26590.125 | 4947 | 3298
196 | Connections to existing sanitary sewer manholes | 1 | CONN | 864.3 | 864.3 | 576.2 | 576.2 | 1440.5 | 1440.5 | 804 | 536
197 | Connections to new building w/ 4" pumped sewer | 1 | CONN | 2580 | 2580 | 1720 | 1720 | 4300 | 4300 | 2400 | 1600
198 | Re Route Gas Service |  |  |  | 0 |  | 0 |  |  |  | 0
199 | Remove existing gas line | 119 | LF |  | 0 | 33.325 | 3965.675 | 33.325 | 3965.675 | 0 | 31
200 | Gas Valve | 2 | EA | 1935 | 3870 | 1290 | 2580 | 3225 | 6450 | 1800 | 1200
201 | New gas services piping '3" Gas Pipe w/ 3' cover | 396 | LF | 51.6 | 20433.6 | 34.4 | 13622.4 | 86 | 34056 | 48 | 32
202 | Connections to existing gas line | 2 | CONN | 2580 | 5160 | 1720 | 3440 | 4300 | 8600 | 2400 | 1600
203 | Shut offs | 2 | CONN | 1935 | 3870 | 1290 | 2580 | 3225 | 6450 | 1800 | 1200
204 | Steam Service |  |  |  | 0 |  | 0
205 | Demolition: |  |  |  | 0 |  | 0
206 | Cap the underground pipe | 2 | EA |  | 0 | 483.75 | 967.5 | 483.75 | 967.5 | 0 | 450
207 | Demolish steam line back to manhole | 251 | LF |  | 0 | 37.625 | 9443.875 | 37.625 | 9443.875 | 0 | 35
208 | New Work: |  |  |  | 0 |  | 0
209 | Equipment |  |  |  | 0 |  | 0
210 | Steam manhole | 2 | EA | 10320 | 20640 | 6880 | 13760 | 17200 | 34400 | 9600 | 6400
211 | Pipe end cap | 1 | EA | 53.75 | 53.75 | 430 | 430 | 483.75 | 483.75 | 50 | 400
212 | Connect new Underground Pipe to existing | 3 | EA | 967.5 | 2902.5 | 645 | 1935 | 1612.5 | 4837.5 | 900 | 600
213 | Piping |  |  |  | 0 |  | 0
214 | Concrete anchor block for steam pipe | 7 | EA | 107.5 | 752.5 | 430 | 3010 | 537.5 | 3762.5 | 100 | 400
215 | Guide for steam pipe | 2 | EA | 43 | 86 | 64.5 | 129 | 107.5 | 215 | 40 | 60
216 | 6" CWS&R Underground | 144 | LF | 60.9095 | 8770.968 | 91.3642 | 13156.452 | 152.2737 | 21927.42 | 56.66 | 84.99
217 | 6" MPS Underground | 480 | LF | 178.407 | 85635.36 | 118.938 | 57090.24 | 297.345 | 142725.6 | 165.96 | 110.64
218 | 4" MPS Underground | 219 | LF | 144.867 | 31725.873 | 96.578 | 21150.582 | 241.445 | 52876.455 | 134.76 | 89.84
219 | New 4" Steam piping - include all trenching and backfill | 145 | LF | 144.867 | 21005.715 | 96.578 | 14003.81 | 241.445 | 35009.525 | 134.76 | 89.84
220 | 2-1/2" PCR Underground | 480 | LF | 86.559 | 41548.32 | 57.706 | 27698.88 | 144.265 | 69247.2 | 80.52 | 53.68
221 | New 2" Glycol piping - include all trenching and backfill | 145 | LF | 55.5281 | 8051.5673 | 37.0187 | 5367.7115 | 92.5468 | 13419.2788 | 51.654 | 34.436
222 | New 2" condenser piping - include all trenching and backfill | 145 | LF | 55.5281 | 8051.5673 | 37.0187 | 5367.7115 | 92.5468 | 13419.2788 | 51.654 | 34.436
223 | 2" PCR Underground | 219 | LF | 55.5281 | 12160.6429 | 37.0187 | 8107.0953 | 92.5468 | 20267.7383 | 51.654 | 34.436
224 | 1" MPC line | 623 | LF | 41.925 | 26119.275 | 27.95 | 17412.85 | 69.875 | 43532.125 | 39 | 26
225 | 1" MW line | 144 | LF | 41.925 | 6037.2 | 27.95 | 4024.8 | 69.875 | 10062 | 39 | 26
226 | Dry Well |  |  |  | 0 |  | 0
227 | Demolition: |  |  |  | 0 |  | 0
228 | Remove stormwater line | 76 | LF |  | 0 | 53.75 | 4085 | 53.75 | 4085 | 0 | 50
229 | Remove catch basin | 2 | LF |  | 0 | 537.5 | 1075 | 537.5 | 1075 | 0 | 500
230 | Equipment: |  |  |  | 0 |  | 0
231 | Construct new curb inlets | 6 | EA | 2257.5 | 13545 | 1505 | 9030 | 3762.5 | 22575 | 2100 | 1400
232 | Relocate existing field inlets | 1 | EA | 1161 | 1161 | 774 | 774 | 1935 | 1935 | 1080 | 720
233 | New drywells | 13 | EA | 8570.0505 | 111410.6565 | 5713.367 | 74273.771 | 14283.4175 | 185684.4275 | 7972.14 | 5314.76
234 | New catch basin | 1 | EA | 940.625 | 940.625 | 1746.875 | 1746.875 | 2687.5 | 2687.5 | 875 | 1625
235 | Relocate existing dry wells | 2 | EA | 6407.9524 | 12815.9049 | 4271.9683 | 8543.9366 | 10679.9207 | 21359.8415 | 5960.886 | 3973.924
236 | Piping: |  |  |  | 0 |  | 0
237 | 10" Storm pipe | 14 | LF | 129 | 1806 | 86 | 1204 | 215 | 3010 | 120 | 80
238 | 15" HDPE pipe | 946 | LF | 23.22 | 21966.12 | 62.78 | 59389.88 | 86 | 81356 | 21.6 | 58.4
239 | Storm water connection to existing drywells | 1 | EA | 1076.4211 | 1076.4211 | 717.6141 | 717.6141 | 1794.0352 | 1794.0352 | 1001.322 | 667.548
240 | Connections: |  |  |  | 0 |  | 0 |  |  |  | 0
241 | New connections to existing main | 3 | Conn | 3160.5 | 9481.5 | 2107 | 6321 | 5267.5 | 15802.5 | 2940 | 1960
242 | Drainage at cooling tower |  |  |  | 0 |  | 0 |  |  |  | 0
243 | Perforated ABS piping to with filter fabric to cooling tower footings, including 6" deep crushed stone | 291 | LF | 16.125 | 4692.375 | 10.75 | 3128.25 | 26.875 | 7820.625 | 15 | 10
244 |  |  |  |  | 0 |  | 0
245 | Additional Sanitary Scope |  |  |  | 0 |  | 0
246 | New Sanitary Manhole MH#1 and MH#3 ( including excavation and back fill) | 2 | EA | 5318.025 | 10636.05 | 3545.35 | 7090.7 | 8863.375 | 17726.75 | 4947 | 3298
247 | Furnish and install new sanitary manhole chamber ( including excavation and backfill) | 1 | EA | 2580 | 2580 | 1720 | 1720 | 4300 | 4300 | 2400 | 1600
248 | Furnish and install 12" sanitary pipe with 18" PVC casing filled with concrete | 162 | LF | 36.12 | 5851.44 | 49.88 | 8080.56 | 86 | 13932 | 33.6 | 46.4
249 | Excavation and backfill as required for pipe | 225 | CY |  | 0 | 37.625 | 8465.625 | 37.625 | 8465.625 | 0 | 35
250 | Pavements to be restored due to installation of the pipe or manhole | 350 | SF | 8.6 | 3010 | 12.9 | 4515 | 21.5 | 7525 | 8 | 12
251 | Grass or landscaping restoration | 1290 | SF | 2.15 | 2773.5 | 3.225 | 4160.25 | 5.375 | 6933.75 | 2 | 3
252 |  |  |  |  | - | 0 | - |  | - | 0 | 0
253 | Subtotal 02-00-06 Utilities-Plumbing |  |  |  | 642827.726 | 0 | 595424.7087 |  | 1238252.4348 | 0 | 0
254 | [5 empty] | 0 |  |  |  | 0 | 0
255 | 02-00-07 Utilities- Heating/Cooling |  |  |  |  | 0 |  |  |  | 0 | 0
256 | [5 empty] | 0 |  |  |  | 0 | 0
257 |  |  |  |  | - | 0 | - |  | - | 0 | 0
258 | Subtotal 02-00-07 Utilities- Heating/Cooling |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0
259 | [5 empty] | 0 |  |  |  | 0 | 0
260 | 02-00-08 Utilities- Electrical |  |  |  |  | 0 |  |  |  | 0 | 0
261 | [5 empty] | 0 |  |  |  | 0 | 0
262 | DEMO WORKS
263 | Remove Duct Bank - 13.2KV | 160 | LF |  | 0 | 37.2488 | 5959.8 | 37.2488 | 5959.8 | 0 | 34.65
264 | Manhole | 1 | EA |  | 0 | 446.985 | 446.985 | 446.985 | 446.985 | 0 | 415.8
265 | Remove Duct Bank - 2.4KV | 605 | LF |  | 0 | 29.799 | 18028.395 | 29.799 | 18028.395 | 0 | 27.72
266 | Remove Other Duct Bank | 86 | LF |  | 0 | 29.799 | 2562.714 | 29.799 | 2562.714 | 0 | 27.72
267 | Remove Light Pole | 2 | EA |  | 0 | 297.99 | 595.98 | 297.99 | 595.98 | 0 | 277.2
268 | Removal of Light Pole Conduit & Wiring | 210 | LF |  | 0 | 14.8995 | 3128.895 | 14.8995 | 3128.895 | 0 | 13.86
269 |  |  |  |  | 0 |  | 0
270 | NEW WORKS |  |  |  | 0 |  | 0
271 | Site Power Equipment |  |  |  | 0 |  | 0
272 | Liquid Filled - 750KVA - 13.2KVA - 277/480V - 3Ph,4W( Outdoor Pad Mtd ) | 1 | EA | 45150 | 45150 | 11919.6 | 11919.6 | 57069.6 | 57069.6 | 42000 | 11088
273 | Manhole | 1 | EA | 8385 | 8385 | 5959.8 | 5959.8 | 14344.8 | 14344.8 | 7800 | 5544
274 |  |  |  |  | 0 |  | 0
275 | Power Feeders |  |  |  | 0 |  | 0
276 | Incoming Power - EMH26A to EMH26D-3#2( 15KV,133%EPR 4"PVC SCH 80) DB-(1'-16" X1'-6")(2A,2SP) |  |  |  | 0 |  | 0
277 | 4"PVC SCH 80 | 1148 | LF | 5.5426 | 6362.9209 | 30.4993 | 35013.1694 | 36.0419 | 41376.0903 | 5.1559 | 28.3714
278 | 3#2( 15KV,133%EPR ) | 574 | LF | 19.35 | 11106.9 | 8.9397 | 5131.3878 | 28.2897 | 16238.2878 | 18 | 8.316
279 | Concrete | 27.2119 | CY | 193.5 | 5265.4933 | 372.4875 | 10136.0747 | 565.9875 | 15401.568 | 180 | 346.5
280 | Excavation & Backfill | 81.6356 | CY |  | 0 | 104.2965 | 8514.3027 | 104.2965 | 8514.3027 | 0 | 97.02
281 | Splicing at Existing MH | 2 | Locs | 1935 | 3870 | 446.985 | 893.97 | 2381.985 | 4763.97 | 1800 | 415.8
282 |  |  |  |  | 0 |  | 0
283 | 750KVA to MDP - 4 Sets - 4#350MCM, #3/0 - 4"PVC Sch 80 DB - (1'-6" X 2' ) ( 4A, 2SP ) |  |  |  | 0 |  | 0
284 | 4"PVC SCH 80 | 450 | LF | 5.5426 | 2494.1763 | 30.4993 | 13724.6744 | 36.0419 | 16218.8507 | 5.1559 | 28.3714
285 | #350MCM | 1200 | LF | 7.8823 | 9458.7134 | 7.6145 | 9137.4462 | 15.4968 | 18596.1596 | 7.3323 | 7.0833
286 | #3/0 | 300 | LF | 3.6082 | 1082.47 | 5.483 | 1644.9048 | 9.0912 | 2727.3748 | 3.3565 | 5.1005
287 | Concrete | 8.8889 | CY | 193.5 | 1720 | 372.4875 | 3311 | 565.9875 | 5031 | 180 | 346.5
288 | Excavation & Backfill | 26.6667 | CY |  | 0 | 104.2965 | 2781.24 | 104.2965 | 2781.24 | 0 | 97.02
289 |  |  |  |  | 0 |  | 0
290 | Temporary Power Equipment |  |  |  | 0 |  | 0
291 | 225A - Circuit Breaker ( NEMA 3R ) | 1 | EA | 1935 | 1935 | 446.985 | 446.985 | 2381.985 | 2381.985 | 1800 | 415.8
292 | 150KVA - 480-120/208V - 3Ph, 4W - Outdoor Mounted | 1 | EA | 12255 | 12255 | 3873.87 | 3873.87 | 16128.87 | 16128.87 | 11400 | 3603.6
293 | 600A - 120/208V - 3Ph, 4W - Temporary Power Panel | 1 | EA | 9997.5 | 9997.5 | 4171.86 | 4171.86 | 14169.36 | 14169.36 | 9300 | 3880.8
294 |  |  |  |  | 0 |  | 0
295 | Temporary Power Feeders |  |  |  | 0 |  | 0
296 | Temporary Feeder - 750KVA to 225A CB and 225A CB, 150KVA X'fmer to Temp Power Panel | 50 | LF | 7.74 | 387 | 37.2488 | 1862.4375 | 44.9888 | 2249.4375 | 7.2 | 34.65
297 | Power to Fire Pump,PPHC Panel |  |  |  | 0 |  | 0 |  |  | 0 | 0
298 | 2"PVC | 315 | LF | 1.2353 | 389.1208 | 15.2496 | 4803.636 | 16.4849 | 5192.7568 | 1.1491 | 14.1857
299 | #6 | 267 | LF | 0.61641 | 164.5824 | 2.1092 | 563.1691 | 2.7257 | 727.7516 | 0.57341 | 1.9621
300 | #10 | 89 | LF | 0.25031 | 22.2777 | 1.3708 | 121.9971 | 1.6211 | 144.2748 | 0.23285 | 1.2751
301 | #1 | 504 | LF | 1.9139 | 964.6294 | 3.4269 | 1727.15 | 5.3408 | 2691.7794 | 1.7804 | 3.1878
302 | #8 | 126 | LF | 0.40016 | 50.4199 | 1.7134 | 215.8938 | 2.1136 | 266.3137 | 0.37224 | 1.5939
303 | Concrete | 7.1056 | CY | 193.5 | 1374.925 | 372.4875 | 2646.7306 | 565.9875 | 4021.6556 | 180 | 346.5
304 | Excavation & Backfill | 21.3167 | CY |  | 0 | 104.2965 | 2223.2537 | 104.2965 | 2223.2537 | 0 | 97.02
305 |  |  |  |  | 0 |  | 0
306 | SITE COMMUNICATIONS |  |  |  | 0 |  | 0
307 |  |  |  |  | 0 |  | 0
308 | Site Security Infra |  |  |  | 0 |  | 0
309 | 1" PVC with concrete encasement | 465 | LF | 21.5 | 9997.5 | 43 | 19995 | 64.5 | 29992.5 | 20 | 40
310 |  |  |  |  | 0 |  | 0
311 | 4-4" PVC |  |  |  | 0 |  | 0
312 | 4" PVC | 2560 | LF | 3.5217 | 9015.552 | 30.544 | 78192.576 | 34.0657 | 87208.128 | 3.276 | 28.413
313 | Concrete | 53.3333 | CY | 193.5 | 10320 | 372.4875 | 19866 | 565.9875 | 30186 | 180 | 346.5
314 | Excavation and Back fill | 160 | CY |  | 0 | 104.2965 | 16687.44 | 104.2965 | 16687.44 | 0 | 97.02
315 | Communication Manholes | 3 | EA | 4515 | 13545 | 2979.9 | 8939.7 | 7494.9 | 22484.7 | 4200 | 2772
316 |  |  |  |  | 0 |  | 0
317 | 4-4" PVC, 2 - 2"PVC |  |  |  | 0 |  | 0
318 | 4" PVC | 380 | LF | 3.5217 | 1338.246 | 30.544 | 11606.7105 | 34.0657 | 12944.9565 | 3.276 | 28.413
319 | 2" PVC | 190 | LF | 1.2353 | 234.7078 | 15.2496 | 2897.4313 | 16.4849 | 3132.139 | 1.1491 | 14.1857
320 | Concrete | 10.7755 | CY | 193.5 | 2085.0521 | 372.4875 | 4013.7253 | 565.9875 | 6098.7773 | 180 | 346.5
321 | Excavation and Back fill | 32.3264 | CY |  | 0 | 104.2965 | 3371.5292 | 104.2965 | 3371.5292 | 0 | 97.02
322 |  |  |  |  | 0 |  | 0
323 | 2 - 2"PVC |  |  |  | 0 |  | 0
324 | 2" PVC | 170 | LF | 1.2353 | 210.0017 | 15.2496 | 2592.4385 | 16.4849 | 2802.4402 | 1.1491 | 14.1857
325 | Concrete | 0.78704 | CY | 193.5 | 152.2917 | 372.4875 | 293.1615 | 565.9875 | 445.4531 | 180 | 346.5
326 | Excavation and Back fill | 2.3611 | CY |  | 0 | 104.2965 | 246.2556 | 104.2965 | 246.2556 | 0 | 97.02
327 |  |  |  |  | 0 |  | 0
328 | Site Lighting |  |  |  | 0 |  | 0
329 | FX1 | 9 | EA | 733.1973 | 6598.7757 | 193.6935 | 1743.2415 | 926.8908 | 8342.0172 | 682.044 | 180.18
330 | FX2 | 20 | EA | 387 | 7740 | 238.392 | 4767.84 | 625.392 | 12507.84 | 360 | 221.76
331 | FX2A | 2 | EA | 311.4447 | 622.8894 | 216.0427 | 432.0855 | 527.4874 | 1054.9749 | 289.716 | 200.97
332 | FX3 | 26 | EA | 433.44 | 11269.44 | 201.1433 | 5229.7245 | 634.5833 | 16499.1645 | 403.2 | 187.11
333 | FX3A | 22 | EA | 477.3 | 10500.6 | 201.1433 | 4425.1515 | 678.4433 | 14925.7515 | 444 | 187.11
334 | FX4 w/ Foundations | 23 | EA | 4014.48 | 92333.04 | 893.97 | 20561.31 | 4908.45 | 112894.35 | 3734.4 | 831.6
335 | FX4A w/ Foundations | 20 | EA | 5476.05 | 109521 | 1042.965 | 20859.3 | 6519.015 | 130380.3 | 5094 | 970.2
336 | FX4B w/ Foundations | 3 | EA | 5476.05 | 16428.15 | 1042.965 | 3128.895 | 6519.015 | 19557.045 | 5094 | 970.2
337 | FX5 w/ Foundations | 5 | EA | 2634.18 | 13170.9 | 595.98 | 2979.9 | 3230.16 | 16150.8 | 2450.4 | 554.4
338 | FX6 | 188 | FT | 122.55 | 23039.4 | 67.0478 | 12604.977 | 189.5978 | 35644.377 | 114 | 62.37
339 | FX7 | 16 | LF | 196.08 | 3137.28 | 52.1483 | 834.372 | 248.2283 | 3971.652 | 182.4 | 48.51
340 | FX7A | 16 | LF | 206.4 | 3302.4 | 52.1483 | 834.372 | 258.5482 | 4136.772 | 192 | 48.51
341 | FX8 | 8 | EA | 1030.71 | 8245.68 | 372.4875 | 2979.9 | 1403.1975 | 11225.58 | 958.8 | 346.5
342 | FX8A | 8 | EA | 1030.71 | 8245.68 | 372.4875 | 2979.9 | 1403.1975 | 11225.58 | 958.8 | 346.5
343 | FX9 | 13 | EA | 548.25 | 7127.25 | 297.99 | 3873.87 | 846.24 | 11001.12 | 510 | 277.2
344 | FX10 | 1 | EA | 1007.49 | 1007.49 | 223.4925 | 223.4925 | 1230.9825 | 1230.9825 | 937.2 | 207.9
345 | 1"PVC | 3359 | LF | 0.58747 | 1973.2983 | 10.966 | 36834.9015 | 11.5535 | 38808.1998 | 0.54648 | 10.201
346 | 2"PVC | 104 | LF | 1.2353 | 128.4716 | 15.2496 | 1585.9624 | 16.4849 | 1714.434 | 1.1491 | 14.1857
347 | 1"RGS | 1010 | LF | 4.2065 | 4248.5615 | 21.0753 | 21286.0962 | 25.2818 | 25534.6576 | 3.913 | 19.605
348 | 2"EMT( Inside Building to Panel Site Lighting Panel ) | 142 | LF | 3.2278 | 458.3438 | 17.1344 | 2433.0883 | 20.3622 | 2891.4322 | 3.0026 | 15.939
349 | 1"EMT( Inside Building to Panel OLR ) | 428 | LF | 1.3622 | 583.0387 | 11.9941 | 5133.4737 | 13.3563 | 5716.5125 | 1.2672 | 11.1573
350 | #8 | 8732 | LF | 0.40016 | 3494.1797 | 1.7134 | 14961.7799 | 2.1136 | 18455.9596 | 0.37224 | 1.5939
351 | #10 | 8194 | LF | 0.2451 | 2008.3494 | 1.341 | 10987.7853 | 1.5861 | 12996.1347 | 0.228 | 1.2474
352 | Concrete | 20.5215 | CY | 193.5 | 3970.9067 | 372.4875 | 7643.9953 | 565.9875 | 11614.902 | 180 | 346.5
353 | Excavation & Backfill | 61.5644 | CY |  | 0 | 104.2965 | 6420.9561 | 104.2965 | 6420.9561 | 0 | 97.02
354 |  |  |  |  | 0 |  | 0
355 | Lighting Control |  |  |  | 0 |  | 0
356 | Ruggedized Sensor w/ Wall Mounting Kit | 60 | EA | 174.15 | 10449 | 148.995 | 8939.7 | 323.145 | 19388.7 | 162 | 138.6
357 |  |  |  |  | 0 |  | 0
358 | Mechanical Feeders(CT) |  |  |  | 0 |  | 0
359 | 1"PVC | 97 | LF | 0.58747 | 56.9842 | 10.966 | 1063.7051 | 11.5535 | 1120.6893 | 0.54648 | 10.201
360 | #12 | 388 | LF | 0.1419 | 55.0572 | 1.043 | 404.6704 | 1.1849 | 459.7276 | 0.132 | 0.9702
361 | Concrete | 0.89815 | CY | 193.5 | 173.7917 | 372.4875 | 334.549 | 565.9875 | 508.3406 | 180 | 346.5
362 | Excavation & Backfill | 2.6944 | CY |  | 0 | 104.2965 | 281.0211 | 104.2965 | 281.0211 | 0 | 97.02
363 |  |  |  |  | - | 0 | - |  | - | 0 | 0
364 | Subtotal 02-00-08 Utilities- Electrical |  |  |  | 519224.4381 | 0 | 537019.3056 |  | 1056243.7437 | 0 | 0
365 | [5 empty] | 0 |  |  |  | 0 | 0
366 | 02-00-09 Planting |  |  |  |  | 0 |  |  |  | 0 | 0
367 | [5 empty] | 0 |  |  |  | 0 | 0
368 | Surface treatment:
369 | Seeded Lawn area w/ stripping and stockpiling topsoil, placing 6" top soil and scarifying existing subgrade upto 4", 9" lawn soil and lawn | 42265 | SF | 0.95675 | 40437.0387 | 1.4298 | 60428.3838 | 2.3865 | 100865.4225 | 0.89 | 1.33
370 | Planting area w/ stripping and stockpiling top soil, placing 6" topsoil and scarifying existing subgrade upto 6", 24" planting soil and 2" shredded hardwood mulch | 3074 | SF | 1.8275 | 5617.735 | 2.752 | 8459.648 | 4.5795 | 14077.383 | 1.7 | 2.56
371 |  |  |  |  | 0 |  | 0
372 | Carpark Area |  |  |  | 0 |  | 0
373 | Seeded lawn area | 37675 | SF | 0.95675 | 36045.5563 | 1.4298 | 53865.8313 | 2.3865 | 89911.3875 | 0.89 | 1.33
374 | Extra-over seeded lawn area for Planting area w/ stripping and stockpiling top soil, placing 6" topsoil and scarifying existing subgrade upto 6", 24" planting soil and 2" shredded hardwood mulch | 567 | SF | 0.8815 | 499.8105 | 1.3115 | 743.6205 | 2.193 | 1243.431 | 0.82 | 1.22
375 |  |  |  |  | 0 |  | 0
376 | Trees: |  |  |  | 0 |  | 0
377 | Shadblow - 7' - 8'ht/ B&B, Full, Multi-trunk | 2 | EA | 361.2 | 722.4 | 541.8 | 1083.6 | 903 | 1806 | 336 | 504
378 | Heritage River Birch - 3" cal / B&B / Branching at 6'ht, Single-trunk | 3 | EA | 361.2 | 1083.6 | 541.8 | 1625.4 | 903 | 2709 | 336 | 504
379 | Heritage River Birch - 8'-10' ht/ B&B /Multi- trunk | 1 | EA | 408.5 | 408.5 | 698.75 | 698.75 | 1107.25 | 1107.25 | 380 | 650
380 | Forest Pansy Redbud - 8' -10'ht/ 2-2 1/2" cal./ B&B/Branching at 5'ht | 13 | EA | 408.5 | 5310.5 | 698.75 | 9083.75 | 1107.25 | 14394.25 | 380 | 650
381 | Sweet bay Magnolia - 7' - 8' ht/ B&B/ Multi-trunk/ Full | 3 | EA | 361.2 | 1083.6 | 541.8 | 1625.4 | 903 | 2709 | 336 | 504
382 | White Oak - 2 1/2" - 3" cal./ min, 12' - 14' ht/ B&B/ Branching at 6' ht. | 4 | EA | 408.5 | 1634 | 645 | 2580 | 1053.5 | 4214 | 380 | 600
383 | Green Giant' Arborvitae - 7' - 8'ht/ B&B | 17 | EA | 361.2 | 6140.4 | 541.8 | 9210.6 | 903 | 15351 | 336 | 504
384 | Shadblow - 7' - 8'ht/ B&B, Full, Multi-trunk | 10 | EA | 361.2 | 3612 | 541.8 | 5418 | 903 | 9030 | 336 | 504
385 | Swamp White Oak - 2 1/2" - 3" cal./ min, 12' - 14' ht/ B&B/ Branching at 6' ht. | 5 | EA | 408.5 | 2042.5 | 645 | 3225 | 1053.5 | 5267.5 | 380 | 600
386 | Flowering Dogwood - 7' - 8' ht/ B&B | 2 | EA | 361.2 | 722.4 | 541.8 | 1083.6 | 903 | 1806 | 336 | 504
387 |  |  |  |  | 0 |  | 0
388 | Shrubs/Vines: |  |  |  | 0 |  | 0
389 | Dwarf Deutzia - 3 gal container | 186 | EA | 47.3 | 8797.8 | 70.95 | 13196.7 | 118.25 | 21994.5 | 44 | 66
390 | Dwarf Fothergilla - 30" - 36" ht/ 7 gallon min | 18 | EA | 47.3 | 851.4 | 70.95 | 1277.1 | 118.25 | 2128.5 | 44 | 66
391 | Smooth Hydrangea - 24" - 30" ht/ 7 gallon min | 7 | EA | 47.3 | 331.1 | 70.95 | 496.65 | 118.25 | 827.75 | 44 | 66
392 | Compact Inkberry - 30" - 36" ht/ 7 gallon min | 73 | EA | 47.3 | 3452.9 | 70.95 | 5179.35 | 118.25 | 8632.25 | 44 | 66
393 | Olympis Wedding Mountain Laurel - 30" - 36" ht/ B&B/ Fully branched from top to bottom | 5 | EA | 47.3 | 236.5 | 70.95 | 354.75 | 118.25 | 591.25 | 44 | 66
394 |  |  |  |  | 0 |  | 0
395 | Herbaceous Perennials/Groundcovers: |  |  |  | 0 |  | 0
396 | Thread Leaf Blue Star - 1 Gal./ fully rooted, 1 yr.-old plant, plant 15" o.c. | 250 | EA | 17.2 | 4300 | 25.8 | 6450 | 43 | 10750 | 16 | 24
397 |  |  |  |  | 0 |  | 0
398 | Grasses: |  |  |  | 0 |  | 0
399 | Sedge - 1 Gal./ fully rooted, 1 yr-old plant, plant 15" o.c. | 300 | EA | 4.3 | 1290 | 6.45 | 1935 | 10.75 | 3225 | 4 | 6
400 | Ruby Muhly - 1 Gal./ fully rooted, 1 yr-old plant, plant 15" o.c. | 355 | EA | 4.3 | 1526.5 | 6.45 | 2289.75 | 10.75 | 3816.25 | 4 | 6
401 | Switch Grass - 3 Gal./ fully rooted, 1 yr-old plant, plant 24" o.c. | 212 | EA | 4.3 | 911.6 | 6.45 | 1367.4 | 10.75 | 2279 | 4 | 6
402 | Creeping broadleaf sedge - 1 Gal./ fully rooted, 1 yr-old plant, plant 15" o.c. | 32 | EA | 4.3 | 137.6 | 6.45 | 206.4 | 10.75 | 344 | 4 | 6
403 | Common periwinkle - 1 Gal./ fully rooted, 1 yr-old plant, plant 12" o.c. | 206 | EA | 4.3 | 885.8 | 6.45 | 1328.7 | 10.75 | 2214.5 | 4 | 6
404 |  |  |  |  | - | 0 | - |  | - | 0 | 0
405 | Subtotal 02-00-09 Planting |  |  |  | 128081.2405 | 0 | 193213.3835 |  | 321294.624 | 0 | 0
406 | [5 empty] | 0 |  |  |  | 0 | 0
407 | 02-00-10 Abatement |  |  |  |  | 0 |  |  |  | 0 | 0
408 | Cost as Provided by abatement consultant | 1 | LS | 20964.435 | 20964.435 | 83857.74 | 83857.74 | 104822.175 | 104822.175 | 19501.8 | 78007.2
409 | [5 empty] | 0 |  |  |  | 0 | 0
410 |  |  |  |  | - | 0 | - |  | - | 0 | 0
411 | Subtotal 02-00-10 Abatement |  |  |  | 20964.435 | 0 | 83857.74 |  | 104822.175 | 0 | 0
412 | [5 empty] | 0 |  |  |  | 0 | 0
The End
[5 empty] | 3338950.4094 |  | 4452186.1121 |  | 7791136.5215
[5 empty] | 3338950.4094 |  | 4452186.1121 |  | 7791136.5215
0

## ECM-SUM
COLLEGE OF TECHNOLOGY AT FARMINGDALE |  |  |  |  | 2021-03-08
NET ZERO CARBON STUDY | [5 empty] | 2021-03-08
Energy Conservation Measures (ECM}
ID | Name | Description | Performance |  | Additional notes | Total Amount
|  |  | Code Requirement / Baseline | Proposed
Envelope
E1 | High performance triple-glazing windows | High performance triple glazed windows filled with argon. | U-0.38 SHGC-0.36 VT-0.40 | System: U-0.31; SHGC-0.24; VT-0.50 Center-of-glass : U-0.27;SHGC-0.27; VT-0.58 | Triple glazing, e=0.05 on surface 2 and 4, LE LE CLR. Insulated vinyl frame, 1/ 2" air, 1/4" glass Manufacturers: Viracon, Interpane | 336271.3377
E2 | Electrochromic glazing | Replace existing windows with electrochromic glazing to optimize solar gain and lighting levels. | U-0.38 SHGC-0.36 VT-0.40 | U-0.28 SHGC-0.09-0.41 VT-0.01-0.60 | SageGlass: 4mm clear w/SR2.0,0.89mm SentryGlas, 2.2mm SageGlass, 12mm air space w/90% Argon fill, 6mm clear Other manufacturers: View Glass, Halio by Kenestral | 506378.5803
E3 | Roof lnsulation (Passive House level) | Replace existing roof with R-60 continuous insulation to achieve Passive House certified values. | U-0.032 R-30ci | R-60c.i. |  | 206022.6355
E4 | Wall insulation | Increase wall insulation to R-30 to achieve Passive House certified level wall construction. | U-0.064 R-13+R-7.5ci | R-30c.i. |  | 315529.5481
E5 | Below-grade wall insulation | Increase below-grade wall insulation to R-15c.i. | C-0.119 R-7.5ci | R-15c.i. |  | 342350.0246
E6 | Reduced infiltration | Provide air-vapor barrier to achieve infiltration rates at Passive House (PHIUS+ 2015) levels | 0.40 cfm /sf_f@ 0.3 in (75 Pa) | 0.05 cfm/sf_f@ 50 Pa |  | 63253.1622
E7 | Internal shading |  | NR | Add internal shading and control to reduce solar heat gain | Black-out shades to provide reduced net amount of solar gain into the space | 45211.0031
Lighting
L1a | Upgrade interior lighting to be 20-30% better than baseline (With DALI) | Optimize interior lighting layout to achieve 20-30% better than 100% CD baseline | Total lighting load (inclusive of code exemptions/allowances) | 20-30% improvement from total lighting load (inclusive of code exemptions/ allowances) | To meet goal, the following will be required to ensure both energy efficient and visually viable results: -Downward revision of Classroom/Meeting Rm./Training Rm. avg. maintained lighting criteria from 40fc to 30-35fc. - Utilization of higher reflectance (+83%) lay in ceiling tile modules (Armstrong Calla, Ultima, Lyra, Optima) - Changing furniture/table top specifications in offices and classrooms to employ lighter value /higher reflectance materials (i.e. white or very light colors) - Re-specificationof most currently specified LED products to reflect higher efficacies - Re-specification of the currently designed 0-lOV lighting control system to reflect the use of the DALI (Digital Addressable Lighting Interface) based or comparable control system to allow for a Lumen Maintenance control protocol to be introduced - Con figuration of local controls in Offices and Classrooms to prevent activation of artificial lighting systems when average daylight levels in these rooms are above an average of 40fc | 262472.5504
L1b | Upgrade interior lighting to be 20-30% better than baseline (With Out DALI) | Optimize interior lighting layout to achieve 20-30% better than 100% CD baseline | Total lighting load (inclusive of code exemptions/allowances) | 20-30% improvement from total lighting load (inclusive of code exemptions/ allowances) | To meet goal, the following will be required to ensure both energy efficient and visually viable results: -Downward revision of Classroom/Meeting Rm./Training Rm. avg. maintained lighting criteria from 40fc to 30-35fc. - Utilization of higher reflectance (+83%) lay in ceiling tile modules (Armstrong Calla, Ultima, Lyra, Optima) - Changing furniture/table top specifications in offices and classrooms to employ lighter value /higher reflectance materials (i.e. white or very light colors) - Re-specificationof most currently specified LED products to reflect higher efficacies - Re-specification of the currently designed 0-lOV lighting control system to reflect the use of the DALI (Digital Addressable Lighting Interface) based or comparable control system to allow for a Lumen Maintenance control protocol to be introduced - Con figuration of local controls in Offices and Classrooms to prevent activation of artificial lighting systems when average daylight levels in these rooms are above an average of 40fc | 14790.9601
L2 | Upgrade exterior lighting to be 20-30% better than baseline | Optimize exterior lighting layout to achieve 20-30% better than 100% CD baseline | Total lighting load (inclusive of code exemptions/allowances) | 20-30% improvement from total lighting load (inclusive of code exemptions/ allowances) |  | Excluded
Plug Loads
P2 | Plug Load Control | Add controllable outlets to manage plug loads to comply with ASHRAE 90.1- 2016 requirements. | NR | 50% of 125 V receptacles in applicable spaces to be off20 mins after occupants leave space |  | 158838.3687
P3 | Load reduction | Reduce effective space load by 20%,e.g. by limiting the amount of time that equipment not in use is on | NR | 20% Equipment Power Density reduction, or equivalent reduction in the amount of time plug loads are on |  | By Owner
Data Center
D1 | Reduce Data Center by 15% | Reduce Data Center energy usage by 15% through strategies involving consolidating IT system redundancies, upgrading Energy Star certified servers, and migrating to a cloud service. | NR | Reduced datacenter load by 15% | Need feedback from IT consultant / ownership: what level of reduction is feasible (if any)? | By Owner
HVAC
H1 | Centralized GS HVAC | Centralized GSHP (HR chiller) + central AHU, VAV w/reheat (hydro) | Minimum efficiency requirements for HYAC | Provide HYAC with performance that is at least 10% better than code |  | Reflected as Concept Estimate
H2 | Centralized AS HVAC | Centralized ASHP (air-cooled HR chiller) + central AHU, VAV w/ reheat (hydro) | Minimum efficiency requirements for HYAC | Provide HVAC with performance that is at least 10% better than code |  | Reflected as Concept Estimate
H3 | Distributed HP HVAC | Air-cooled chiller and electric boiler serving a condenser water loop. Condenser loop serves distributed heat pumps conditioning spaces+ DOAS | Minimum efficiency requirements for HYAC | Provide HVAC with performance that is at least 10% better than code |  | Reflected as Concept Estimate
Controls
C1 | Demand Control Ventilation | Add demand control ventilation to reduce heating and cooling loads . | Where required by code | Applicable to all spaces |  | 166886.2531
C2 | Relax setpoints | Relax setpoints in transient spaces (corridors) from heating and cooling setpoints of 72F and 75F to 68F and 80F. |  | Relax setpoints |  | By Operation
Water
W1 | Low Flow Faucets & Fixtures | Upgrade to low flow faucets and fixtures to conserve water and reduce DHW loads. |  | Kitchen faucet: 1.5 gpm Restroom faucet 0.35 gpm Shower: 1.5 gpm |  | 13014.7479

## ECM-SUM (2) (hidden)
| COLLEGE OF TECHNOLOGY AT FARMINGDALE |  |  |  | 2021-03-08
NET ZERO CARBON STUDY
Concept Estimate
State University Construction Fund Construct School of Applied Social Sciences State University College of Technology at Farmingdale
Energy Conservation Measures (ECM}
ID | Name | Description | Performance |  | Additional notes | Total Amount
|  |  | Code Requirement / Baseline | Proposed
Envelope
El- | High performance triple-glazing windows | High performance triple glazed windows filled with argon. | U-0.38 SHGC-0.36 VT-0.40 | System: U-0.31; SHGC-0.24; VT-0.50 Center-of-glass : U-0.27;SHGC-0.27; VT-0.58 | Triple glazing, e=0.05 on surface 2 and 4, LE LE CLR. Insulated vinyl frame, 1/ 2" air, 1/4" glass Manufacturers: Viracon, Interpane | 336271.3377
E2- | Electrochromic glazing | Replace existing windows with electrochromic glazing to optimize solar gain and lighting levels. | U-0.38 SHGC-0.36 VT-0.40 | U-0.28 SHGC-0.09-0.41 VT-0.01-0.60 | SageGlass: 4mm clear w/SR2.0,0.89mm SentryGlas, 2.2mm SageGlass, 12mm air space w/90% Argon fill, 6mm clear Other manufacturers: View Glass, Halio by Kenestral | 506378.5803
E3- | Rooflnsulation (Passive House level) | Replace existing roof with R-60 continuous insulation to achieve Passive House certified values. | U-0.032 R-30ci | R-60c.i. |  | 206022.6355
E4- | Wall insulation | Increase wall insulation to R-30 to achieve Passive House certified level wall construction. | U-0.064 R-13+R-7.5ci | R-30c.i. |  | 315529.5481
E5- | Below-grade wall insulation | Increase below-grade wall insulation to R-15c.i. | C-0.119 R-7.5ci | R-15c.i. |  | 342350.0246
E6- | Reduced infiltration | Provide air-vapor barrier to achieve infiltration rates at Passive House (PHIUS+ 2015) levels | 0.40 cfm /sf_f@ 0.3 in (75 Pa) | 0.05 cfm/sf_f@ 50 Pa |  | 63253.1622
E7- | Internal shading |  | NR | Add internal shading and control to reduce solar heat gain | Black-out shades to provide reduced net amount of solar gain into the space | 45211.0031
Lighting
L1- | Upgrade interior lighting to be 20-30% better than baseline | Optimize interior lighting layout to achieve 20-30% better than 100% CD baseline | Total lighting load (inclusive of code exemptions/allowances) | 20-30% improvement from total lighting load (inclusive of code exemptions/ allowances) | To meet goal, the following will be required to ensure both energy efficient and visually viable results: -Downward revision of Classroom/Meeting Rm./Training Rm. avg. maintained lighting criteria from 40fc to 30-35fc. - Utilization of higher reflectance (+83%) lay in ceiling tile modules (Armstrong Calla, Ultima, Lyra, Optima) - Changing furniture/table top specifications in offices and classrooms to employ lighter value /higher reflectance materials (i.e. white or very light colors) - Re-specificationof most currently specified LED products to reflect higher efficacies - Re-specification of the currently designed 0-lOV lighting control system to reflect the use of the DALI (Digital Addressable Lighting Interface) based or comparable control system to allow for a Lumen Maintenance control protocol to be introduced - Con figuration of local controls in Offices and Classrooms to prevent activation of artificial lighting systems when average daylight levels in these rooms are above an average of 40fc | 262472.5504
L2- | Upgrade exterior lighting to be 20-30% better than baseline | Optimize exterior lighting layout to achieve 20-30% better than 100% CD baseline | Total lighting load (inclusive of code exemptions/allowances) | 20-30% improvement from total lighting load (inclusive of code exemptions/ allowances) |  | #REF!
Plug Loads
P2- | Plug Load Control | Add controllable outlets to manage plug loads to comply with ASHRAE 90.1- 2016 requirements. | NR | 50% of 125 V receptacles in applicable spaces to be off20 mins after occupants leave space |  | 158838.3687
P3- | Load reduction | Reduce effective space load by 20%,e.g. by limiting the amount of time that equipment not in use is on | NR | 20% Equipment Power Density reduction, or equivalent reduction in the amount of time plug loads are on |  | #REF!
Data Center
1- | Reduce Data Center by 15% | Reduce Data Center energy usage by 15% through strategies involving consolidating IT system redundancies, upgrading Energy Star certified servers, and migrating to a cloud service. | NR | Reduced datacenter load by 15% | Need feedback from IT consultant / ownership: what level of reduction is feasible (if any)? | #REF!
HVAC
Hl- | Centralized GS HVAC | Centralized GSHP (HR chiller) + central AHU, VAV w/reheat (hydro) | Minimum efficiency requirements for HYAC | Provide HYAC with performance that is at least 10% better than code |  | #REF!
H2- | Centralized AS HVAC | Centralized ASHP (air-cooled HR chiller) + central AHU, VAV w/ reheat (hydro) | Minimum efficiency requirements for HYAC | Provide HVAC with performance that is at least 10% better than code |  | #REF!
H3- | Distributed HP HVAC | Air-cooled chiller and electric boiler serving a condenser water loop. Condenser loop serves distributed heat pumps conditioning spaces+ DOAS | Minimum efficiency requirements for HYAC | Provide HVAC with performance that is at least 10% better than code |  | #REF!
Controls
Cl- | Demand Control Ventilation | Add demand control ventilation to reduce heating and cooling loads . | Where required by code | Applicable to all spaces |  | 166886.2531
C2- | Relax setpoints | Relax setpoints in transient spaces (corridors) from heating and cooling setpoints of 72F and 75F to 68F and 80F. |  | Relax setpoints |  | #REF!
Water
Wl- | Low Flow Faucets & Fixtures | Upgrade to low flow faucets and fixtures to conserve water and reduce DHW loads. |  | Kitchen faucet: 1.5 gpm Restroom faucet 0.35 gpm Shower: 1.5 gpm |  | 13014.7479

## ECM-EST
COLLEGE OF TECHNOLOGY AT FARMINGDALE
Farmingdale, New York
| Energy Conservation Methods (ECM) |  |  |  | 2021-03-08
| Description | Qty | Unit | Unit Rate | Amount
1
2 | E1 High performance triple-glazing windows
3
4 | ADD
5 | High performance triple glazed windows w/ insulated vinyl frame, 1/2" air, 1/4" glass | 2533 | SF | 120.92 | 306290.36
6 | High performance triple glazed windows w/ insulated vinyl frame, 1/2" air, 1/4" glass at curtain wall | 1974 | SF | 204.09 | 402873.66
7 | High performance triple glazed windows w/ insulated vinyl frame, 1/2" air, 1/4" glass at Storefront | 6260 | SF | 126.21 | 790074.6
8 | Allow for 3/4" shear studs | 2000 | EA | 5.37 | 10740
9 | DEDUCT
10 | Exterior Wall Type 1 - 3 1/4" Thermally broken aluminum framed fixed windows with 1" insulated glass including metal infill panels (at exterior masonry walls) Double glazed - See drawing A-210 | -2533 | SF | 100.92 | -255630.36
11 | Exterior full height Curtainwall - vision and spandrel panels - 1" insulated spandrel glazing / 2 1/2" galv metal stud / vapor barrier Double glazed- see sections 1, 7 & 8 on drawing A-215 | -1974 | SF | 184.09 | -363393.66
12 | Exterior Type SF glass storefront system including all aluminum mullions at first to third floors - see sections SF-1 to SF- 64 on drawings A-211 to A-214 | -6260 | SF | 106.21 | -664874.6
13 |  |  |  |  | -
14 | Subtotal |  |  |  | 226080
15 | Markup | 48.74% |  |  | 110191.3377
16 |  |  |  |  | -
17 | Total E1 High performance triple-glazing windows |  |  |  | 336271.3377
18
19 | E2 Electrochromic glazing
20 | ADD
21 | Electrochromic glazing at exterior windows | 2533 | SF | 35.322 | 89470.626
22 | Electrochromic glazing at curtainwall | 1974 | SF | 64.4315 | 127187.781
23 | Electrochromic glazing at Storefront | 6260 | SF | 37.1735 | 232706.11
24 | DEDUCT
25 | Motorized Shades at classrooms ( including power, control and wiring as required) | -2533 | SF | 43 | -108919
26 |  |  |  |  | -
27 | Subtotal |  |  |  | 340445.517
28 | Markup | 48.74% |  |  | 165933.0633
29 |  |  |  |  | -
30 | Total E2 Electrochromic glazing |  |  |  | 506378.5803
31
32 | E3 Roof lnsulation (Passive House level)
33 | ADD
34 | Increase in reinforced concrete parapet wall 8" | 10.89 | CY | 996.14 | 10847.9462
35 | Rigid insulation increase to R-60 | 15958 | SF | 8 | 127664
36 | Second floor roof area - 2,085 SF includes canopies
37 | Main roof area/ Clerestory - 13,379 SF
38 | Stair Bulkhead roof area - 494 SF
39 |  |  |  |  | -
40 | Subtotal |  |  |  | 138511.9462
41 | Markup | 48.74% |  |  | 67510.6893
42 |  |  |  |  | -
43 | Total E3 Roof lnsulation (Passive House level) |  |  |  | 206022.6355
44
45 | E4 Wall insulation
46 | ADD
47 | Rigid insulation increase from 3" to 6" | 21263 | SF | 5 | 106315
48 | UHPC window returns | 1442 | LF | 35 | 50470
49 | Steel for bent plates and relieving angles | 7 | TON | 6450 | 45150
50 | Structural thermal breaks at permieter (assume thermal break every 20LF) | 102 | EA | 100 | 10200
51 |  |  |  |  | -
52 | Subtotal |  |  |  | 212135
53 | Markup | 48.74% |  |  | 103394.5481
54 |  |  |  |  | -
55 | Total E4 Wall insulation |  |  |  | 315529.5481
56
57 | E5 Below-grade wall insulation
58 | ADD
59 | Concrete foundation walls at perimeter of basement and areaways walls include all formwork and reinforcing ( 16' height) | 133.4 | CY | 1259.98 | 168081.332 | 0.28571
60 | Continuous concrete wall footings supporting building foundation walls at basement ( 2' deep ) , at areaway foundation walls ( 2.5') -include all formwork and reinforcing | 18.135 | CY | 1006.2 | 18247.437 | 0.064516
61 | 14" thick Perimeter grade wall (refer to detail B/S-500 or A/S-503) - 526 LF | 27.115 | CY | 1008.64 | 27349.2736 | 0.28571
62 | Perimeter Grade wall foundation ( 2' wide x 1' deep) - 492 LF | 9.1 | CY | 775.75 | 7059.325 | 0.25
63 | Rigid insulation board (R7.5ci to R15ci ) at basement foundation walls - 4' down only | 1900 | SF | 2.355 | 4474.5
64 | Rigid Insulation (R7.5ci to R15ci ) at perimeter grade beam | 2104 | SF | 2.355 | 4954.92
65 |  |  |  |  | -
66 | Subtotal |  |  |  | 230166.7876
67 | Markup | 48.74% |  |  | 112183.237
68 |  |  |  |  | -
69 | Total E5 Below-grade wall insulation |  |  |  | 342350.0246
70
71 | E6 Reduced infiltration
72
73 | Provide air vapor barrier to achieve infiltration rates (increase from 0.4cfm/sf to 0.05cfm/sf) | 21263 | SF | 2 | 42526
74 |  |  |  |  | -
75 | Subtotal |  |  |  | 42526
76 | Markup | 48.74% |  |  | 20727.1622
77 |  |  |  |  | -
78 | Total E6 Reduced infiltration |  |  |  | 63253.1622
79
80 | E7 Internal shading
81 | ADD
82 | Blackout shades at exterior windows | 2533 | SF | 12 | 30396
83 |  |  |  |  | -
84 | Subtotal |  |  |  | 30396
85 | Markup | 48.74% |  |  | 14815.0031
86 |  |  |  |  | -
87 | Total E7 Internal shading |  |  |  | 45211.0031
88
89 | L1a Upgrade interior lighting to be 20-30% better than baseline (With DALI)
90 | ADD
91 | ELA | 1 | LS | 73706.4 | 73706.4
92 | SDA | 1 | LS | 3924 | 3924
93 | ELS | 1 | LS | 349884 | 349884
94 | Damin | 1 | LS | 3864 | 3864
95 | International Lights | 1 | LS | 231055.2 | 231055.2
96 | F1 | 212 | EA | 234.6645 | 49748.874
97 | F1A | 72 | EA | 234.6645 | 16895.844
98 | F3 | 151 | LF | 70.4025 | 10630.7775
99 | F3A | 66 | LF | 70.4025 | 4646.565
100 | F4 | 38 | EA | 203.3745 | 7728.231
101 | F5 | 35 | EA | 211.197 | 7391.895
102 | F5B | 44 | EA | 312.8895 | 13767.138
103 | F5C | 4 | EA | 469.3395 | 1877.358
104 | F6 | 13 | EA | 312.8895 | 4067.5635
105 | F6A | 16 | EA | 312.8895 | 5006.232
106 | F7 | 18 | EA | 534.2845 | 9617.121
107 | F7A | 28 | EA | 250.3095 | 7008.666
108 | F8 | 14 | EA | 211.197 | 2956.758
109 | F8A | 55 | EA | 211.197 | 11615.835
110 | F9 | 16 | EA | 195.552 | 3128.832
111 | F11 | 6 | EA | 203.3745 | 1220.247
112 | F12 | 16 | EA | 226.842 | 3629.472
113 | F14 | 139 | EA | 54.7575 | 7611.2925
114 | F15 | 467 | LF | 62.58 | 29224.86
115 | F17 | 44 | EA | 234.6645 | 10325.238
116 | F17A | 41 | EA | 203.3745 | 8338.3545
117 | F20 | 6 | EA | 39.1125 | 234.675
118 | F20A | 11 | EA | 39.1125 | 430.2375
119 | F21 | 23 | LF | 120.886 | 2780.378
120 | F21A | 17 | LF | 120.886 | 2055.062
121 | FX2 | 14 | EA | 250.3095 | 3504.333
122 | 1"EMT | 17805.3333 | LF | 13.3563 | 237814.0413
123 | #12 - Lights | 53416 | LF | 1.1849 | 63290.7488
124 | #12 - DALI | 53416 | LF | 1.1849 | 63290.7488
125
126 | DEDUCT
127 | F1 | -298 | EA | 697.5675 | -207875.115
128 | F1A | -122 | EA | 697.5675 | -85103.235
129 | F3 | -165.04 | LF | 176.6977 | -29162.1967
130 | F3A | -44.55 | LF | 176.6977 | -7871.8848
131 | F4 | -36 | EA | 400.0935 | -14403.366
132 | F5 | -68 | EA | 446.2432 | -30344.541
133 | F5B | -45 | EA | 1845.99 | -83069.55
134 | F5C | -3 | EA | 2250.5125 | -6751.5375
135 | F6 | -13 | EA | 1764.6684 | -22940.6892
136 | F6a | -16 | EA | 1764.6684 | -28234.6944
137 | F7 | -18 | EA | 424.6035 | -7642.863
138 | F7a | -27 | EA | 1374.667 | -37116.009
139 | F8 | -17 | EA | 394.6433 | -6708.9353
140 | F8a | -55 | EA | 394.6433 | -21705.3787
141 | F9 | -17 | EA | 399.0938 | -6784.5938
142 | F11 | -5 | EA | 703.2435 | -3516.2175
143 | F12 | -20 | EA | 783.6427 | -15672.855
144 | F14 | -223.27 | LF | 248.2283 | -55421.9214
145 | F15 | -620.48 | LF | 207.1418 | -128527.313
146 | F15a | -16.72 | LF | 207.1418 | -3463.4101
147 | F17 | -44 | EA | 662.0925 | -29132.07
148 | F17A | -16 | EA | 522.6435 | -8362.296
149 | F20 | -30.16 | LF | 230.7488 | -6959.3823
150 | F20a | -24 | LF | 230.7488 | -5537.97
151 | F21a | -14.77 | LF | 108.7986 | -1606.9553
152 | F21 | -14.87 | LF | 108.7986 | -1617.8352
153 | 3/4"EMT | -14750.79 | LF | 11.3784 | -167841.0527
154 | #12 | -44252.37 | LF | 1.1849 | -52433.0844
155 |  |  |  |  | -
156 | Subtotal |  |  |  | 176464.0263
157 | Markup | 48.74% |  |  | 86008.5241
158 |  |  |  |  | -
159 | Total L1a Upgrade interior lighting to be 20-30% better than baseline (With DALI) |  |  |  | 262472.5504
160
161
162 | L1b Upgrade interior lighting to be 20-30% better than baseline (With Out DALI)
163
164 | ADD
165 | ELA | 1 | LS | 58022.4 | 58022.4
166 | SDA | 1 | LS | 2988 | 2988
167 | ELS | 1 | LS | 332284.8 | 332284.8
168 | Damin | 1 | LS | 3864 | 3864
169 | International Lights | 1 | LS | 209767.2 | 209767.2
170 | F1 | 212 | EA | 223.49 | 47379.88
171 | F1A | 72 | EA | 223.49 | 16091.28
172 | F3 | 151 | LF | 67.05 | 10124.55
173 | F3A | 66 | LF | 67.05 | 4425.3
174 | F4 | 38 | EA | 193.69 | 7360.22
175 | F5 | 35 | EA | 201.14 | 7039.9
176 | F5B | 44 | EA | 297.99 | 13111.56
177 | F5C | 4 | EA | 446.99 | 1787.96
178 | F6 | 13 | EA | 297.99 | 3873.87
179 | F6A | 16 | EA | 297.99 | 4767.84
180 | F7 | 18 | EA | 424.6 | 7642.8
181 | F7A | 28 | EA | 238.39 | 6674.92
182 | F8 | 14 | EA | 201.14 | 2815.96
183 | F8A | 55 | EA | 201.14 | 11062.7
184 | F9 | 16 | EA | 186.24 | 2979.84
185 | F11 | 6 | EA | 193.69 | 1162.14
186 | F12 | 16 | EA | 216.04 | 3456.64
187 | F14 | 139 | EA | 52.15 | 7248.85
188 | F15 | 467 | LF | 59.6 | 27833.2
189 | F17 | 44 | EA | 223.49 | 9833.56
190 | F17A | 41 | EA | 193.69 | 7941.29
191 | F20 | 6 | EA | 37.25 | 223.5
192 | F20A | 11 | EA | 37.25 | 409.75
193 | F21 | 23 | LF | 108.8 | 2502.4
194 | F21A | 17 | LF | 108.8 | 1849.6
195 | FX2 | 14 | EA | 238.39 | 3337.46
196 | 1"EMT | 17805.3333 | LF | 11.3784 | 202597.006
197 | #12 - Lights | 53416 | LF | 1.1849 | 63290.7488
198
199 | DEDUCT
200 | F1 | -298 | EA | 697.5675 | -207875.115
201 | F1A | -122 | EA | 697.5675 | -85103.235
202 | F3 | -165.04 | LF | 176.6977 | -29162.1967
203 | F3A | -44.55 | LF | 176.6977 | -7871.8848
204 | F4 | -36 | EA | 400.0935 | -14403.366
205 | F5 | -68 | EA | 446.2432 | -30344.541
206 | F5B | -45 | EA | 1845.99 | -83069.55
207 | F5C | -3 | EA | 2250.5125 | -6751.5375
208 | F6 | -13 | EA | 1764.6684 | -22940.6892
209 | F6a | -16 | EA | 1764.6684 | -28234.6944
210 | F7 | -18 | EA | 424.6035 | -7642.863
211 | F7a | -27 | EA | 1374.667 | -37116.009
212 | F8 | -17 | EA | 394.6433 | -6708.9353
213 | F8a | -55 | EA | 394.6433 | -21705.3787
214 | F9 | -17 | EA | 399.0938 | -6784.5938
215 | F11 | -5 | EA | 703.2435 | -3516.2175
216 | F12 | -20 | EA | 783.6427 | -15672.855
217 | F14 | -223.27 | LF | 248.2283 | -55421.9214
218 | F15 | -620.48 | LF | 207.1418 | -128527.313
219 | F15a | -16.72 | LF | 207.1418 | -3463.4101
220 | F17 | -44 | EA | 662.0925 | -29132.07
221 | F17A | -16 | EA | 522.6435 | -8362.296
222 | F20 | -30.16 | LF | 230.7488 | -6959.3823
223 | F20a | -24 | LF | 230.7488 | -5537.97
224 | F21a | -14.77 | LF | 108.7986 | -1606.9553
225 | F21 | -14.87 | LF | 108.7986 | -1617.8352
226 | 3/4"EMT | -14750.79 | LF | 11.3784 | -167841.0527
227 | #12 | -44252.37 | LF | 1.1849 | -52433.0844
228 |  |  |  |  | -
229 | Subtotal |  |  |  | 9944.1727
230 | Markup | 48.74% |  |  | 4846.7874
231 |  |  |  |  | -
232 | Total L1b Upgrade interior lighting to be 20-30% better than baseline (With Out DALI) |  |  |  | 14790.9601
233
234 | P2 Plug Load Control
235 | ADD
236 | 120V - Control Panel | 6 | EA | 2397.624 | 14385.744
237 | 3/4"EMT | 900 | LF | 11.3784 | 10240.6005
238 | #12 | 2700 | LF | 1.1849 | 3199.1355
239 | Occupancy Sensor | 30 | EA | 484.94 | 14548.2
240 | LV Wires & Outlet Boxes | 30 | EA | 125.82 | 3774.6
241 | Duplex Receptacle ( 50% Receptacles to LCP ) | 300 | EA | 109.75 | 32925
242 | 3/4"EMT(Power) | 4500 | LF | 11.3784 | 51203.0025
243 | #12 | 13500 | LF | 1.1849 | 15995.6775
244 | 1/2"EMT(Control) | 4500 | LF | 8.6 | 38700
245 | Control Wiring | 15000 | LF | 1.01 | 15150
246 | Duplex Receptacle ( to Ckt Breakers ) | 300 | EA | 109.75 | 32925
247 | 3/4"EMT | 4500 | LF | 11.3784 | 51203.0025
248 | #12 | 13500 | LF | 1.1849 | 15995.6775
249 | DEDUCT |  |  |  | 0
250 | Duplex Receptacle | -319 | EA | 109.7467 | -35009.2133
251 | Duplex Receptacle - GFI | -30 | EA | 135.5661 | -4066.983
252 | Duplex Receptacle - GFI - WP | -17 | EA | 144.996 | -2464.932
253 | Duplex Receptacle - WP | -3 | EA | 148.866 | -446.598
254 | Quad Receptacle | -165 | EA | 151.446 | -24988.59
255 | 30A Receptacle | -3 | EA | 159.386 | -478.1579
256 | Poke Thru - Duplex Receptacle ( Ceiling Mtd ) | -1 | EA | 704.985 | -704.985
257 | Poke Thru - Duplex Receptacle & Tele/Data ( Ceiling Mtd ) | -18 | EA | 918.48 | -16532.64
258 | P- Power Feed ( Electrified Furniture System ) JB | -22 | EA | 181.245 | -3987.39
259 | D- Data Feed ( Electrified Furniture System ) JB | -22 | EA | 181.245 | -3987.39
260 | Ground Pull Box | -3 | EA | 342.495 | -1027.485
261 | 3/4"EMT | -55 | LF | 11.3784 | -625.8145
262 | 2"EMT | -110 | LF | 20.3622 | -2239.8418
263 | 1"EMT | -50 | LF | 13.3563 | -667.8169
264 | 3/4"EMT | -6444 | LF | 11.3784 | -73322.6996
265 | #12 | -19332 | LF | 1.1849 | -22905.8102
266 |  |  |  |  | -
267 | Subtotal |  |  |  | 106789.293
268 | Markup | 48.74% |  |  | 52049.0758
269 |  |  |  |  | -
270 | Total P2 Plug Load Control |  |  |  | 158838.3687
271
272 | C1 Demand Control Ventilation
273
274 | CO2 controls | 102 | EA | 1100 | 112200
275 |  |  |  |  | -
276 | Subtotal |  |  |  | 112200
277 | Markup | 48.74% |  |  | 54686.2531
278 |  |  |  |  | -
279 | Total C1 Demand Control Ventilation |  |  |  | 166886.2531
280
281 | W1 Low Flow Faucets & Fixtures
282
283 | Additional cost for low flow faucets and fixtures | 25 | EA | 350 | 8750
284 |  |  |  |  | -
285 | Subtotal |  |  |  | 8750
286 | Markup | 48.74% |  |  | 4264.7479
287 |  |  |  |  | -
288 | Total W1 Low Flow Faucets & Fixtures |  |  |  | 13014.7479
289
The End